## Slide 1: Line Differential

## Slide 2: Current Differential Principle
End A
Communication Link
End B
Relay A
A
I
B
I
F
I
IA + IB = 0 Healthy
IA + IB ≠ 0 (= IF) Fault
Relay B

## Slide 3: Three Ended Line Protection
C
I
A
I
B
I
F
I
IA + IB + IC = 0 Healthy
IA + IB + IC ≠ 0 (= IF) Fault
End A
End B
End C

## Slide 4: MiCOM P54x All Digital/Numerical Design
0 I I I I I I 0 I 0 . . . . . 0 I 0 I I I I I I 0
Digital messages
A/D
P
Digital communication interface
End A
End B
Relay A
Relay B

## Slide 5: MiCOM P54x Current Differential Elements
Fully numerical design
Use standard 56 or 64 kbits/s comms channel
Also work with dedicated optical fibre links
Phase discrimination
Capacitive charging current compensation
Two and three ended feeder protection
Continuous propagation delay time measurement and compensation
Additional InterMiCOM and permissive intertrip (PIT) commands transfer
  Includes 8 freely-programmable commands (per channel) and status transfer bits between line ends
Powerful error checking for secure signalling

## Slide 6: MiCOM P54x Differential protection
Is1
Percentage bias k1
No trip
I
C
I
B
I
A
Percentage bias k2
Trip
Differential current
│Idiff│ =│IA + IB + IC │
Bias Current
│Ibias│ = ½(│IA │ + │ IB │ + │ IC │)
Is2

## Slide 7
Time Synchronization
Sample alignment

## Slide 8: MiCOM P54x Propagation Delay Problem
Current at B
Current received from A
Propagation delay
Relay A
Relay B

## Slide 9: MiCOM P54x Propagation Delay Time, Measurement - 1
tA1
Data message
Relay B
Relay A
Current
vectors
tA1
tA2
tA3
tA4
tA5
tB1
tB2
tB3
tB4
tB5
tB
*
tp1

## Slide 10: MiCOM P54x Propagation Delay Time, Measurement - 2
Propagation delay time tp = tp1 = tp2 = 1/2 (tA* - tA1 – td)
This calculation is sometimes called “ping-pong” method
Data message
tB1
tB2
tB3
tB4
tB5
tB*
tA1
tA2
tA3
tA4
tp1
tA5
Current
vectors
tA1
tB3*
tA*
Current
vectors
tB3
tA1
td
tp2
td

## Slide 11
Communication Error
Compensation

## Slide 12: MiCOM P54x Transient Change in Propagation Delay
Unequal send (tp1) and receive (tp2) delays result in incorrect vector alignment and hence incorrect differential current
Majority of switched communications networks switch send and receive path simultaneously
Some networks may produce transient period where send/receive paths differ
Potential for relay maloperation

## Slide 13: MiCOM P54x Protection for SONET/SDH Systems
End B
End A
t1
t2
t3
t4
tp1
tp2
td
Current vectors
td
t3
t1
Current vectors
t1
With asynchronous sampling, using the “ping-pong” method is necessary to assume: tp1 = tp2
In order to realign vectors thus allowing phase and magnitude information to be compared at line ends.
BUT: For SONET(Synchronous Optical Network) systems, tp1 can be different than tp2
Notes: Synchronous Optical Networking (SONET) and Synchronous Digital Hierarchy (SDH) are standardized protocols that transfer multiple digital bit streams synchronously over optical fiber using lasers or highly coherent light from light-emitting diodes (LEDs)
SONET and SDH, which are essentially the same, were originally designed to transport circuit mode communications

## Slide 14: MiCOM P54x SONET/SDH Ring, Configuration
Node
5
Node
4
Node
1
Node
2
Node
6
Node
3
Standby
path
Worker path
tp1
tp2
tp1’
tp2’
Line
Relay A
Relay B
Notes: The diagram shows a typical Sonnet/SDH ring.
Normally comms messages will be routed by the worker path. If a channel break occurs in the worker path messages will be re-routed by the protection path.
If one channel is routed by the worker path and the other routed by the protection path a differential comms delay will occur. This will normally occur as part of the comms self healing process when a fault is detected. Under certain circumstances this conditions may be present for a long time.
On some comms systems the difference between the worker path and protection path is greater than 1ms. If this condition is present for more than 1/2 cycle the P541/4 may trip the circuit breaker due to measuring a high differential current.

## Slide 15: MiCOM P54x SONET/SDH, Part Routing via Standby Channel
Node
5
Node
4
Node
1
Node
2
Node
6
Node
3
tp1
tp2
tp1’
tp2’
Line
Relay A
Relay B
Now, tp2 > tp1
Notes: The diagram shows a typical Sonnet/SDH ring.
Normally comms messages will be routed by the worker path. If a channel break occurs in the worker path messages will be re-routed by the protection path.
If one channel is routed by the worker path and the other routed by the protection path a differential comms delay will occur. This will normally occur as part of the comms self healing process when a fault is detected. Under certain circumstances this conditions may be present for a long time.
On some comms systems the difference between the worker path and protection path is greater than 1ms. If this condition is present for more than 1/2 cycle the P541/4 may trip the circuit breaker due to measuring a high differential current.

## Slide 16: MiCOM P54x Transient Change in Propagation Delay (2)
Relay continuously measures the propagation delay
Any change in propagation delay greater than settable value used to raise k1 (initial bias slope) to 200% (effectively blocking relay for currents less than Is2, similar to an overcurrent interlock)
Change is maintained for settable time delay (max. 500ms) to overcome transient period after which k1 is reduced to original value

## Slide 17: MiCOM P54x Transient Change in Propagation Delay (3)
Is1
Percentage bias k1
Percentage bias k2
Differential current
│Idiff│ =│IA + IB + IC │
Bias Current
│Ibias│ = ½(│IA │ + │ IB │ + │ IC │)
Is2
Bias 200%

## Slide 18
Current Differential Communication Link

## Slide 19: MiCOM P54x Direct Optical Fibre Link
OPGW

## Slide 20: MiCOM P54x / MiCOM P59x Interfacing to PCM Multiplexers
850nm multimode
P593
interface
unit
ISDN
X.21 electrical
Multiplexer
G.703 or V.35 electrical
P591/2
interface
unit

## Slide 21: MiCOM P54x / MiCOM P59x Multiplexed Optical Link
34 Mbit/s
Multiplexer
Multiplexer
64k
bits/s
Earth wire optical fibre
Telephone
Telecontrol
Teleprotection
End A
End B

## Slide 22: MiCOM P54x / MiCOM P59x Multiplexed Microwave Link
Multiplexer
Multiplexer
64k
bits/s
Telephone
Telecontrol
Teleprotection
End A
End B

## Slide 23: MiCOM P54x Interfacing Direct Fibre Optic to Multiplexers
850nm multimode
Direct connection no interface!
IEEE C37.94
Multiplexer

## Slide 24: MiCOM P54x Unique Address Function
To avoids maloperation if multiplexers misdirect data messages
Range of addresses for 2 terminal applications
  1A, 1B; 2A, 2B; _ _ _ _ _ 20A, 20B
Range of addresses for 3 terminal applications
  1A, 1B, 1C; 2A, 2B, 2C; _ _ _ _ _20A, 20B, 20C

## Slide 25: MiCOM P54x Communications Path for Two Ended Application
Tx
Rx
End A
Rx
Tx
End B
CH1

## Slide 26: MiCOM P54x Redundant Communications
CH1
CH2
End A
End B
Both channels are active - relays automatically select the correct message should one channel fail
“Hot Standby”

## Slide 27: MiCOM P54x Communications Path for Three Ended Application
P54x
CH1
CH2
Tx
Rx
Rx
Tx
Rx
Tx
Rx
Tx
Tx
Rx
End B
End C
End A
P54x
CH1
CH2
P54x
CH2
CH1
Tx
Rx
Note: Full line protection is provided even should one communications path fail
E.g. For A-B channel fail, C still offers line protection and will intertrip to A and B in the event of a fault
Notes: No InterMiCOM (no pass-through)

## Slide 28: MiCOM P54x Mixed channels for Three Ended Application
P54x
CH1
CH2
Tx
Rx
Rx
Tx
Rx
Tx
Rx
Tx
Tx
Rx
End B
End C
End A
P54x
CH1
CH2
P54x
CH2
CH1
Tx
Rx
End C has 850nm CH1, and 1300nm CH2
End A has 850nm CH2, and 1300nm CH1
CH1 and CH2 can not be inverted by settings
850 nm
1300 nm
1300 nm
Notes: No InterMiCOM (no pass-through)

## Slide 29: Optical Budgets for Direct Optical Connection Between Relays
Short Haul
Long Haul
Notes: .

## Slide 30: Make the most of your energy™