## Slide 1: Distance Protection

## Slide 2: Distance Protection
Popular, widely used on Sub-Transmission and Transmission Systems
Virtually independent of Fault Current Level (ZS/ZL ratios)
Fast Discriminative Protection:- Zone 1 or ‘Aided’ Distance Scheme
Time Delayed Remote Back-Up.

## Slide 3: Overcurrent weakness for line protection:
F1
115kV
50
IF1
ZS = 10 
ZS = 10 
ZL = 4 
IF1 = 115kV/3(5+4) = 7380A
 Is > 7380A

## Slide 4: Advantages of Distance Protection
F2
50
IF2
ZS = 10 
Consider One source is out of service
IF2 = 115kV/3 x 10 = 6640A
 Is <6640A
>7380A - IMPRACTICAL

## Slide 5: Simplified Line Diagram
at FN (60Hz) XC = large
L
R
R
R
R
L
L
L
C
C
C
R
L

## Slide 6: Impedance Seen By Measuring Element
jX
ZL
R

## Slide 7: Basic Principle of Distance Protection
ZL
ZS
Generation
Distance
Relay
IR
21
VR

## Slide 8: Basic Principle of Distance Protection
Relay
PT.
Normal Load
IR
ZL
ZS
VR
VS
ZLOAD

## Slide 9: Basic Principle of Distance Protection
Fault
IR
ZS
VR
VS
ZLOAD
ZL
ZF
Impedance Measured ZR = VR/IR = ZF
Relay Operates if ZF < Z where Z = setting
Increasing VR has a Restraining Effect  VR called Restraining Voltage
Increasing IR has an Operating Effect

## Slide 10: Plain Impedance Characteristic
jX
ZL
R
TRIP
STABLE
Impedance Seen At Measuring Location For Line Faults

## Slide 11: Impedance ratio factor:
IR
21
VR
I1/I2
ZP
V1
V2
VFP
Relays are calibrated in secondary ohms :-

## Slide 12: Example
ZP = 4;
VTR= V1/V2 = 115kV/115V =1000;
CTR= I1/I2 = 600/5A = 120
CTR= I1/I2 = 600/1A = 600
ZR(5) = 4 x (120/1000) = 0.48 -5A Relay
ZR(1) = 4 x (600/1000) = 2.4  -1A Relay

## Slide 13: Input Quantities for - Faults
FAULT VRESTRAINT IOPERATE
A - B VA - VB IA - IB
B - C VB - VC IB - IC
C - A VC - VA IC - IA
VRESTRAINT & IOPERATE are selected inside the relay
No setting adjustments are required apart from

## Slide 14: Neutral Impedance Replica Vectorial Compensation ( A-N fault)
Replica impedance circuit :-
Z1
IRA
IRN
Z1
N
Z1
ZN
Z1 = Phase replica impedance
ZN = Neutral replica impedance
IRA passes through Z1
IRN passes through ZN
ZT = Z1 + ZN

## Slide 15: Neutral Impedance Compensation (reference calculation)
For a single phase to ground fault the total earth loop impedance is given by : - (Z1 + Z2 + Z0)/3 = ZT
ZT = (Z1 + Z2 + Z0)/3 = Z1 + ZN ( in replica circuit)
ZN = (Z1 + Z2 + Z0)/3 - Z1
= (2Z1 + Z0)/3 - Z1
= - Z1 + Z0 = KN Z1
3
3

## Slide 16: Distance Characteristics

## Slide 17: Distance Characteristics
MHO
R
Zn
jX
jX
R
Zs
Zn
CROSS-
POLARISED
MHO
QUADRILATERAL
Zn
R
OFFSET
MHO
jX
Zn′
Zn
R
IMPEDANCE
jX
Zn
R
LENTICULAR
jX
Zn
R
POLYGON
Zn
R

## Slide 18: Self Polarised Mho Relays
Very popular characteristic
Simple
Inherently directional
Operates for F1,
Not for F2 or F3
Settings :- Z = reach setting  = characteristic angle
jX
R
F3
F1
Z

OPERATE
RESTRAIN
F2

## Slide 19: Offset Mho Characteristic:
Normally used as backup protection
Operates for zero faults (close up faults)
Generally time delayed (as not discriminative)
jX
R
Z
-Z’

## Slide 20: Quadrilateral Characteristic
ZL
jX
Z1
Rf
R
Load
R

## Slide 21: Protection Zone

## Slide 22
Zones of Protection
Z2A
Z2C
Z3A
Z3C
Time
T3
T2
Z1C
Z1A
Z1B
D
C
A
Z2B
T2
Z1A = 80% of ZAB
Z2A = 120% of ZAB
Z3A(FORWARD) = 120% of {ZAB + ZCD}
B

## Slide 23
Zones of Protection ( Mho)
R
A
D
C
B
Z1A
Z2A
Z3A
jX

## Slide 24
Zone 1
FAST OPERATION
Trips circuit breaker without delay as soon as
fault within Zone 1 reach is detected.
REACH SETTING
Cannot be set to 100% of protected line or may
overreach into next section.
Overreach caused by possible errors in :-
CTs
VTs
ZLINE information
Relay Measurement

## Slide 25
Zone 1
Possible
Overreach
ZONE 1 = ZL
ZL
F
ZONE 1 = 0.8ZL
ZL
Possible incorrect tripping for fault at ‘F’
 Zone 1 set to  0.8ZL

## Slide 26
Minimum Zone 1 Reach Setting
Dictated by :-
Minimum relay voltage for fault at Zone 1
reach point to ensure accurate measurement.
Minimum voltage depends on relay design typically 1  3 volts.

## Slide 27
Zone 2
Covers last 20% of line not covered by Zone 1.
Provides back-up protection for remote busbars.
To allow for errors :-
  Z2G > 1.2 ZGH
Zone 2 is time delayed to discriminate with Zone 1 on next section for faults in first 20% of next section.
Z1H
Z2G
TIME
Z1G
G
H
F

## Slide 28
Zone 2
Overlap only occurs for faults in first 20% of following line.
Faults at ‘F’ should result in operation of Z1H and tripping of circuit breaker ‘H’.
  If ‘H’ fails to trip possible causes are :-
   Z1H operates but trip relays fail.
  Z2H may operate but will not trip if followed by the same trip relays.
  Fault must be cleared at ‘G’ by Z2G.
  Z1H and trip relays operate but circuit breaker fails to trip.
Zone 2 on adjacent line sections are not normally time graded with each other
Z1G
Z1H
Z2G
Z2H
‘H’
‘G’
F

## Slide 29
Zone 3
Provides back-up for next adjacent line.
Provides back-up protection for busbars (reverse offset).
Actual Zone 3 settings will be scheme specified, i.e. permissive or blocking schemes.
Many modern relays have more than 3 Zones to allow the use of three forward and an independent reverse zone.
H
G
K
Z1G
Z1H
Z2G
Z3G REV
Z3G FWD
Time
Typical settings : Z3FWD > 1.2 x (ZGH + ZHK)
Z3REV 0.1 to 0.25 of Z1G

## Slide 30
Zone Time Coordination - Ideal Situation
Zone 1 :- tZ1 = instantaneous (typically 15 - 35mS)
Zone 2 :- tZ2 = tZ1(down) + CB(down) + Z2(reset) + Margin
e.g. tZ2 = 35 + 100 + 40 + 100 = 275mS
Zone 3 :- tZ3 = tZ2(down) + CB(down) + Z3(reset) + Margin
e.g. tZ3 = 275 + 100 + 40 + 100 = 515mS

## Slide 31: MiCOM Distance features

## Slide 32: MiCOM P54x/P44X Distance protection - Introduction
P54x/P44X Use Superimposed Current
Proven DELTA technology
Compares pre-faulted system
Acts as a fault detector and faulted phase detector
Can quickly recognize evolving faults and power swings
Provides secure phase selection for complex fault conditions
Sensitive to any fault type
Notes: Phase selection is necessary to ensure that the right mho/quad elements according to the fault type are allowed to decide whether to trip.
Phase selection avoids elements on unfaulted phases from tripping, eg:
“A” phase fault presents a “ghost” impedance on phases B and C due to all elements relying on residual current in the fault loop calculation. Operating on the wrong phase risks a single pole trip being converted wrongly to a 3 phase trip, or worse a forward trip for a reverse fault.
As voltage collapses for a single phase fault, this also collapses certain phase-phase voltages (eg A-phase fault reduces Vab and Vca too). With heavy remaining load, this can also risk a three phase trip.
In 3 pole tripping applications, bad phase selection might mean wrong fault flagging (targetting).
Delta I phase selection as in P442 and LFZR is VERY good:
No need to set any I>>, V<, Z< starters to avoid ghost impedances
No settings - the delta is factory set and its sensitivity automatically applied on all systems without any need to set or adjust.

## Slide 33: MiCOM P54x/P44X Faulted = Unfaulted + Superimposed
i
rly
=
i
mem
+
i
r
Prefault
Fault
= Superimposed
Current:-
Notes: The voltage signal (vr) equals the unfaulted voltage (vpr) plus the superimposed voltage (vr ). The current signal (ir) equals the unfaulted current (ipr) plus the superimposed current(ir ). Prior to the fault the superimposed signals are zero. The slide shows a forward fault. Initially the superimposed signals are of opposite polarity, but thereafter the polarity relationship varies with time due to the phase shift introduced by the source angle.

## Slide 34: MiCOM P54x Superimposed Components
2 cycle window
Notes: Phase selectors measure phase to phase: A-B, B-C, C-A.
In this case:
CA is the largest delta
BC is above 80% of the largest delta, and so is “included”
AB is less than 80% of CA delta, so is excluded
The common phase in BC and CA is phase “C”
So it is a C phase ground/earth fault

## Slide 35: MiCOM P54x/P44X Distance Zones, Mho Characteristics
Z3
Zp
Z2
Z1
Z4
Avalable for Phase and Ground Protection (21P and 21G)
Three independent Forward zones
  Z1, Z2, Z3
  Z3 optional forward/reverse offset
One Reverse zone
  Z4
Programmable Fwd/Rev zone
  Zone p
Notes: Zone designations are chosen as per P442 family.
Zone 1, 2 and 3 ALWAYS forward looking.
Zone 4 ALWAYS reverse looking (eg. For use in channel aided schemes as reverse fault signalling).
Zone p is programmable to look FWD or REV.
Note that to ensure tripping for a close-up zero voltage fault, for a switch on to fault (SOTF) where the memory is unavailable, Zone 1 transiently has a reverse offset = 20% of forward reach.
Zone 3 can be set with a forward or reverse offset from the origin, which is set as a percentage of the forward reach (easier than in LFZR).

## Slide 36: Distance Zones, Quatrilateral Characteristics
Avalable for Phase and Ground Protection (21P and 21G)
Independently selectable
  eg. Mho phase + quad ground fault
Z3 (reverse offset)
Zp
(if reverse
looking)
Z4
Z2
Z1
Notes: Zone designations are chosen as per P442 family.
Zone 1, 2 and 3 ALWAYS forward looking.
Zone 4 ALWAYS reverse looking (eg. For use in channel aided schemes as reverse fault signalling).
Zone p is programmable to look FWD or REV.
Note that to ensure tripping for a close-up zero voltage fault, for a switch on to fault (SOTF) where the memory is unavailable, Zone 1 transiently has a reverse offset = 20% of forward reach.
Zone 3 can be set with a forward or reverse offset from the origin, which is set as a percentage of the forward reach (easier than in LFZR).

## Slide 37: MiCOM P54x/P44X Distance protection, loadblinders
Z
R
X
Load Area
Blinder
Angle
Blinder Impedance
Setting
Blinder Allows Stability Notch around Load
Notes: The blinder is basically formed from an underimpedance circle, with radius set by the user; and two blinder lines crossing through the origin.
The blinder cuts a notch out of the side of distance zones, to avoid heavy load.
We always recommend that the blinder should be set, for added security.
Set the blinder angle half way between the worst case power factor angle, and the line impedance angle.
Worst case load angle = (COS) -1 Power Factor
Typical Z< setting is to allow 3 or 4 times full load current to flow.

## Slide 38: MiCOM P54x/P44X Distance protection, Blinder for faults
Better Resisitive Coverage on Fault Inception
R
X
Load Area
Blinder disappears for volts below V<
Rf
Characteristic
Expansion
Z
Notes: The blinder is basically formed from an underimpedance circle, with radius set by the user; and two blinder lines crossing through the origin.
The blinder cuts a notch out of the side of distance zones, to avoid heavy load.
We always recommend that the blinder should be set, for added security.
Set the blinder angle half way between the worst case power factor angle, and the line impedance angle.
Worst case load angle = (COS) -1 Power Factor
Typical Z< setting is to allow 3 or 4 times full load current to flow.

## Slide 39: Channel Dependant Schemes

## Slide 40: Permissive Under reach Scheme (PUR)
Tx Rx
Tx Rx
Send Logic : Z1
Trip Logic : Rx + Z2
Z3
Z2
Z1
1 .
T2
T3
Trip
T2
&
Z3
Z2
Z1
1 .
T2
T3
Trip
T2
&
100
0
100
0
Z3
Z3
Z1
Z1
Z2
Z2

## Slide 41: Permissive Underreach Scheme Time race
A
21
C
B
D
A
C
B
D
Send
Fault
Fault
21
21
21
Race between relay at D picking up and signal send from relay at C resetting, following opening of breaker at C
If signal send from C resets before relay D operates then aided tripping will not occur
To prevent this a 100ms delay on drop off of the signal send is used in the scheme logic
Rx + Z2
Rx + Z2

## Slide 42: Permissive Underreach Transfer Trip Advantages
Scheme is very secure as signalling channel only keyed for internal fault (Zone 1 initiation)

## Slide 43: Permissive Underreach Transfer Trip Disadvantages
If one terminal of the line is open then only Basic scheme logic will apply
If there is a weak infeed at one terminal then only Basic scheme logic will apply
If signalling channel fails then only Basic scheme logic will apply

## Slide 44: Permissive Overreach Scheme (POR) Internal Fault
Z3
Z2
Z1
1 .
T2
T3
Trip
&
T2
Z3
Z2
Z1
1 .
T2
T3
Trip
&
T2
Rx Tx
Rx Tx
Send Logic : Z2
Trip Logic : Rx + Z2
Z3
Z3
Z1
Z1
Z2
Z2

## Slide 45: Permissive Overreach Scheme (POR) External Fault
Z3
Z2
Z1
1 .
T2
T3
Trip
&
T2
Z3
Z2
Z1
1 .
T2
T3
Trip
&
T2
Rx Tx
Rx Tx
Send Logic : Z2
Trip Logic : Rx + Z2
Z3
Z3
Z1
Z1
Z2
Z2

## Slide 46: Permissive Overreach Scheme (CB Echo Logic)
Z3
Z2
Z1
T2
T3
Trip
&
T2
Z3
Z2
Z1
T2
T3
Trip
&
T2
&
1
Rx Tx
CB open
&
1
Rx Tx
CB open
1 .
1 .
Send Logic : Z2
Trip Logic : Rx + Z2
Open terminal echo : CB Open + Rx
Z3
Z3
Z1
Z1
Z2
Z2

## Slide 47: Permissive Overreach Scheme (WI Echo Logic)
Z3
Z2
Z1
T2
T3
Trip
T2
Z3
Z2
Z1
T2
T3
Trip
T2
&
Z4
CB open
&
Z4
CB open
Send Logic : Z2
Trip Logic : Rx + Z2
Open terminal echo : CB Open + Rx
Weak Infeed echo : Z4 + Rx
1
&
&
&
Rx Tx
&
Rx Tx
1 .
1 .
1
Z4
Z4
Z1
Z1
Z2
Z2

## Slide 48: Permissive Overreach Weak Infeed Trip Scheme
Z4
Z4
Z1
Z1
Z2
Z2
Z3
Z2
Z1
T3
Trip
&
T2
&
LDOV
Z3
Z2
Z1
T3
Trip
&
T2
&
LDOV
&
Rx Tx
Z4
CB open
&
Rx Tx
Z4
CB open
&
&
1 .
1 .
1
1
Send Logic : Z2
Trip Logic : Rx + Z2
Open terminal echo : CB Open + Rx
Weak Infeed echo : Z4 + Rx
Weak Infeed trip : Z4 + LDOV reset + Rx

## Slide 49: Permissive Overreach Transfer Trip Advantages
Provides better resistive coverage, especially on short lines, where MHO measuring elements are used
For cases where one line terminal is open, open breaker echo logic can be used
For cases of weak or zero infeed at one line terminal weak infeed logic can be used (reverse looking zone required)

## Slide 50: Permissive Overreach Current reversal Guard
For double circuit lines, the fault current direction can change in one circuit when circuit breakers open sequentially to clear the fault on the parallel circuit.
The change in current direction causes the overreaching distance elements to see the fault in the opposite direction to the direction in which the fault was initially detected (settings of these elements exceed 150% of the line impedance at each terminal).
The race between operation and resetting of the overreaching distance elements at each line terminal can cause the Permissive Overreach, to trip the healthy line.
Line L1 close to circuit breaker B, as circuit breaker B trips it causes the direction of current flow in line L2 to reverse.

## Slide 51: Current reversal guard:
A time delay tREVERSAL GUARD is required in case the overreaching trip element at end D operates before the signal send from the relay at end C has reset. Otherwise this would cause the relay at D to over trip.

## Slide 52: Blocking Schemes

## Slide 53: Blocking Scheme - Internal Fault
Z3
Z2
Z1
T3
Trip
&
T2
&
Rx Tx
1 .
Z3
Z3
Z1
Z1
Z2
Z2
Z3
Z2
Z1
T2
T3
Trip
&
T2
&
Rx Tx
1 .
Send Logic : Z3 + Z2
Trip Logic : Rx + Z2

## Slide 54: Blocking Scheme - External Fault
Z3
Z2
Z1
T3
Trip
&
T2
&
Rx Tx
1 .
Z3
Z3
Z1
Z1
Z2
Z2
Z3
Z2
Z1
T2
T3
Trip
&
T2
&
Rx Tx
1 .
Send Logic : Z3 + Z2
Trip Logic : Rx + Z2

## Slide 55: Blocking Scheme - Advantages
Fast tripping will still be possible at closed end of line for all fault positions with remote breaker open
Fast tripping will still be possible at strong infeed terminal for all fault positions where remote terminal has no or weak infeed

## Slide 56: Blocking Scheme - Disadvantages
Historically only 2 forward zones of protection available (unless relay has >3 Zones)
If signalling channel fails supervision must revert the relay back to Basic scheme logic

## Slide 57: Make the most of your energy™