National Transmission & Despatch Company Limited

(National Power Control Center)

DC BIPOLE LOW POWER COMMISSIONING DESPATCH PROCEDURE OF

MATIARI & LAHORE CONVERTER STATION

±660kV HVDC MATIARI-LAHORE, PROJECT, PAKISTAN

15022021-NPCC-DCDP V 1.9

February, 2021

| DC BIPOLE LOW POWER COMISSIOINING DESPATCH PROCEDURE OF MATIARI & LAHORE CONVERTER STATION ±660kV HVDC MATIARI-LAHORE, PROJECT, PAKISTAN (V 1.9) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Document Number |  |  | : | 15022021-NPCC-DCDP V 1.9 |  |
| Reference Document Number PMLTC/CET |  |  | : | Matiari-Lahore ±660kV HVDC Transmission Project Commissioning Tests-Bipole Low Power System Tests ProgramV4-updated 29-01-2020 |  |
| Issue Date |  |  | : | 15-02-2021 |  |
| Prepared by: |  |  |  |  | NPCC |
| Review by NTDC Working Group: |  |  |  |  |  |
| Review by M/S HATCH: |  |  |  |  |  |
| Review by PMLTC: |  |  |  |  |  |
| Review by M/S CESI: |  |  |  |  |  |
| Approved by Commissioning Committee: |  |  |  |  |  |
| Engr. Muhammad Ayub General Manager System Operation NPCC |  | Dr. Chang Yong Chief Engineer (PMLTC) |  |  | Mr. Aldo Danielli Independent Engineer M/S CESI |
| Sign: |  | Sign: |  |  | Sign: |
| Disseminated for information and implementation to all concerned. |  |  |  |  |  |

Table of Contents

1	General Conditions	4

2	Pre-requisites to the commissioning:	6

3	Energization and Clearance Certificate for Equipment Status	7

3.1	Provision of Clearance Certificate by PMLTC/CE HVDC NTDC to NPCC	7

4	Safety Precautions during Commissioning Tests:	7

5	Commissioning Procedure:	8

6	Disturbance Handling:	8

7	Equipment Status Report (ESR) before start of commissioning tests:	8

8	Commissioning Test Startup Procedure:	9

8.1	Initial Operation Tests, Joint Power Control, Normal Power Direction, Bi-Pole Ground Return	9

8.2	Pole Compensation, Joint Power Control, Normal Power Direction, Bi-Pole Ground Return	9

8.3	Automatic Power Curve Control Test, Joint Power Control, Bi-Pole Ground Return	9

8.4	Normal/Reduced Voltage Operation, Joint Power Control, Bi-Pole Ground Return	9

8.5	Backup Control, Joint Power Control, Bi-Pole Ground Return	9

8.6	Pole Compensation by Disturbance tests, Joint Power Control, Normal Power Direction, Bi-Pole Ground Return	9

8.7	Operation with Station Ground Test, Joint Power Control, Normal Power Direction, Bi-Pole Ground Return	9

8.8	Disturbances, Joint Power Control, Bi-Pole Ground Return	9

8.9	Frequency Control Test, Joint Power Control, Bi-Pole Ground Return	10

8.10	Initial Operation Tests, Bi-Pole Ground Return Operation, Reversed Power Direction, Joint Power Control	10

8.11	Protective Trip X, Y, and Z, Reversed Power Direction, Joint Power Control, Normal Power Direction, Bi-Pole Ground Return	10

8.12	Pole Compensation and disturbance test, Reversed Power Direction, Joint Power Control, Bi-Pole Ground Return	10

8.13	AC/DC Line Faults, Joint Power Control, Bi-Pole Ground Return	10

References

- Matiari-Lahore ±660kV HVDC Transmission Project Commissioning Tests-Bipole Low Power System Tests ProgramV4-updated 29-01-2021

- Lahore Converter station SLD document number DCL00, dated: 17-08-2020, Rev-00.

- Matiari Converter station SLD document number DCM01, dated: 13-10-2020, Rev-01.

# General Conditions

  - This dispatch procedure is issued for operational co-ordination during “Commissioning Tests Plan” of the HVDC System/switchyard at both Matiari/Lahore Converter stations of ±660kV HVDC Matiari –Lahore project as per reference information provided by Pakistan Matiari Lahore Transmission Company (PMLTC) through CE HVDC [1].

  - Scope of this dispatch procedure includes first-time energization/testing/the commissioning of DC system in the HVDC switchyard at ±660kV Matiari and Lahore Converter station.

  - The authorized representatives from PMLTC and NPCC (list of despatcher on duty and key personnel to be provided later) shall confirm in writing the revision number of the Commissioning Test Plans [1] to be followed throughout the testing prior to start of testing. Any changes made to the test plan once testing has started shall be noted and approved in writing by both the authorized representatives from PMLTC and NPCC.

  - The authorized personnel (2 personnel) as identified by PMLTC shall remain at NPCC during whole DC commissioning period.

  - PMLTC shall provide the 24/7 duty roster along with names/designation of authorized operational staff of Matiari and Lahore converter station to NPCC.

  - It shall be the responsibility of PMLTC and Test Director to establish desired safe communications during entire commissioning period with the authorized control room operators at Matiari-Lahore Converter station regarding requirement of switching etc. for the scheduled test item.

  - The operator at Matiari and Lahore Converter Station shall be well conversant with the prudent practices and SOPs regarding compliance to the instructions of system operator (NPCC authorized dispatcher on duty).

  - CET/PMLTC shall attach this dispatch procedure (15022021-NPCC-DCDP V 1.9), including its all annexures with commissioning test program.

  - The commissioning director appointed by CET shall be responsible for coordination and compliance of NPCC Instructions.

  - The test director(s) shall re-submit final adjusted test plan three days in advance at 10:00 Hrs to NPCC along with Sequence of Operation (SOO) and re-confirm the next day test plan one day in advance at 10:00 Hrs every day.

  - The test schedule (time and date) of each test item of the DC station system/switchyard of the Lahore and Matiari Converter stations shall be approved by General Manager (System Operations, NPCC) with mutual understanding of PMLTC/CE HVDC NTDC one day before commencement of the test.

  - It shall be the discretion of NPCC to carry out all operations/switching through remote control whether through passing telephonic instructions to control room operators at concerned substations or by NPCC system operator himself through SCADA/OWS in presence of Chinese expert at NPCC.

  - Prior to each test, the test director (XIE GUOPING) of China Electric Power Research Institute shall notify the relevant departments, participating in test, through the tele-conference call system dial-in number (to be determined), in the converter station.

  - The test director shall be identified by PMLTC prior to the start of testing daily.

  - The NPCC authorized dispatcher on duty shall be identified by NPCC prior to the start of testing daily.

  - NPCC shall manage the AC system parameters according to the requirements of the commissioning (as mentioned in commissioning program).

  - Operators of Matiari and Lahore converter stations are responsible for equipment status report and the execution of the operation orders issued by NPCC.

  - The test director(s) shall seek permission from NPCC regarding switching of any HVAC and HVDC switchgear(s) to meet the test requirement as per agreed test activity of the commissioning program.

  - NPCC upon request of Test Director shall impart instructions to the authorized operational personnel on duty in control room of Matiari and Lahore Converter stations. The communication procedure shall be as follows:

- NPCC authorized dispatcher shall identify themselves.

- NPCC authorized dispatcher shall state the instruction to be followed

- Operation personnel on duty in the control room of Matiari and Lahore Converter station shall identify themselves.

- Operation personnel on duty in the control room of Matiari and Lahore Converter stations shall acknowledge the instruction by repeating the instruction back to the authorized NPCC dispatcher, to re-confirm the instruction.

- NPCC authorized dispatcher shall confirm the instruction to be followed and approve execution.

- Operation personnel on duty in the control room of Matiari and Lahore Converter stations shall acknowledge confirmation to execute the operation.

- Operation personnel on duty in the control room of Matiari and Lahore Converter stations shall then execute the operation and shall inform NPCC after execution.

- NPCC authorized dispatcher shall acknowledge, that operation has been executed, by verifying the status from OWS/ SCADA.

- Any delay in execution of instructions/operations by PMLTC shall be communicated by stating the cause/reason of delay.

- All the communications between NPCC and PMLTC operation personnel shall be recorded on both sides.

# Pre-requisites to the commissioning:

  - PMLTC shall ensure that the final SLDs [2] have been approved and issued by NPCC and equipment’s code in the switchyards, control room panels and relay rooms has been marked as per approved SLDs. The switching sequences during and after the commissioning shall be performed as per Dispatch Code/ nomenclature of the approved SLDs [2].

  - Round the clock healthy voice-communication (Hotline, direct dialing etc..) between the control room of Matiari/Lahore Converter stations and NPCC shall be ensured by PMLTC.

  - CET/PMLTC shall submit commissioning plan along with sequence of operation to NPCC during the commissioning/energization process. CET/PMLTC shall also inform NPCC its possible effects on AC system under operation.

  - PMLTC shall provide the “Power Curves”, which are to be used during commissioning, 3 days prior to the start of commissioning to NPCC.

  - Prior to commissioning, PMLTC and CE HVDC NTDC shall ensure the provision of real time data through OWS and SCADA in NPCC control centers for supervisory control and monitoring.

  - The commissioning test program [1] shall be confirmed by PMLTC and Chief Engineer HVDC, NTDC as the final version.

  - PMLTC shall submit the final version of the commissioning test program document to all related participants, before start of the commissioning test.

  - Chief Engineer HVDC, NTDC will record and issue the list of representatives nominated by all stakeholders and re-issue the changings in list of representatives during commission / testing activities.

  - Chief Engineer HVDC, NTDC shall prepare the methodology to ensure clear coordination and decision making during the commissioning / testing.

  - PMLTC shall provide fully functional Stability Control System to ensure power system stability and reliability during DC commissioning.

  - DC commissioning tests A1, A2 and A3 for Matriari and Lahore converter stations respectively, have been successfully completed, including Open Line Test with DC line, and DC lines of both poles Pole-I and Pole-II have been successfully energized.

  - The results of DC commissioning tests A1, A2 and A3 for Matriari and Lahore converter stations respectively, including all graphs/charts related to pole power, current, voltages, firing angles and extinction angles, tap positions etc... have been approved by all concerned NTDC formations (Asset management, Protection & Control, Project Delivery, TSG, Design department) and Owner Engineer (M/S HATCH).

  - Approval of NTDC authority is required before conducting AC line fault tests.

  - Relevant personnel from Asset Management, protection and control, TSG, CE (HVDC) must be at the site to witness the AC line fault test.

  - Optional tests may or may not be carried out by NPCC as per the then system prevailing conditions

# Energization and Clearance Certificate for Equipment Status

# Provision of Clearance Certificate by PMLTC/CE HVDC NTDC to NPCC

Prior to energization of DC switch yard or any of its component and pre- energization commissioning test(s); PMLTC through CE HVDC, NTDC, shall submit an energization message/clearance certificate (Bipole DC Transmission Line and the relevant component of DC system at Lahore and Matiari Converter stations) along with certificate of Readiness / Synchronization, by the consultant to Director Power Control, NPCC by verifying the following:

- The construction of primary, secondary and auxiliary infrastructure of all equipment involved in the start-up and commissioning of DC Yard at both Matiari and Lahore converter stations have been completed.

- The construction personnel have been evacuated from the site, and the infrastructure construction grounding wires have been removed.

- All required main protection and backup protection have been put into operation, automation, communication, defense lines and remedial actions system etc has been implemented and functioning properly.

- The pre-energization tests including sub system on site tests of the circuit/equipment to be energized have been performed by the concerned formations and results found satisfactory.

- The measuring and debugging equipment required for the system commissioning of DC System substation is ready. The relevant equipment on the measuring point has been connected, and the safety measures have been taken.

- Therefore, NPCC is requested to initiate switching/ operations for energization of ±660kV HVDC Matiari - Lahore system as per approved commissioning program.

- NPCC shall ensure that the AC system is normal and shall allow CET to commence the commissioning test.

- Director Power Control, NPCC shall acknowledge the clearance certificate of the energization.

# Safety Precautions during Commissioning Tests:

Prior to energization of DC switch yard, Bipole DC Transmission Line or any of its component and pre- energization commissioning test(s); PMLTC shall make sure following:

  - During the test, CET/PMLTC is responsible for on-site safety measures at both converter stations to ensure that they do not affect the operation of equipment.

  - During the commissioning of DC system, PMLTC will be responsible for taking on-site safety measures, as per requirement of the commissioning and NEPRA Codes (Power Safety Codes, Grid Codes etc.) and international standards, to ensure equipment and personnel safety at both Matiari and Lahore Converter stations.

  - At Matiari and Lahore converter stations, the test equipment or external equipment should be properly tagged /locked out, or use the black, red and white tape belt and other warning signs/ equipment.

# Commissioning Procedure:

The procedure for the commissioning of DC system is as follows:

  - Commissioning director shall seek formal permission from NPCC before initiating any commissioning test.

  - NPCC will manage the operation of AC system to meet the requirements of commissioning tests as planned for a particular day.

  - If in any case, the commissioning work cannot be carried out in accordance with the commissioning plan due to undesired AC system / Power grid conditions, test plan of that day shall be rescheduled by NPCC, with co-ordination of CE-HVDC and PMLTC.

  - NPCC instructions to be followed by all concerned during the commissioning of HVDC system in view of prevailing system conditions.

# Disturbance Handling:

During the test, CET/PMLTC is responsible for on-site safety measures at both converter stations to ensure human safety and stable operation of equipment. The scope of responsibilities in the event of disturbance handling during the commissioning of DC system is as follows:

  - NPCC is responsible for the switching operation and disturbance management of AC system of the associated grid stations/plants connected with the converter stations, and PMLTC is responsible for the switching operation and disturbance management of Matiari and Lahore Converter stations and Bipole DC Transmission Line.

  - In case there is any problem or equipment fault occurred with the AC system during the commissioning test, NPCC will coordinate with relevant NTDC Asset Management to fix it. In case there is any problem or equipment fault occurred at Matiari and Lahore Converter stations and Bipole DC Transmission Line, PMLTC will fix it.

  - During the commissioning, if any equipment under test depicts abnormal behavior, the commissioning director is responsible for managing the disturbance.

  - During the commissioning, if an emergent situation arises that endangers personal safety and poses serious threat to the main equipment, the operators may not wait for the commissioning director order and is permitted to immediately stop the DC system, and inform NPCC.

  - If the DC system is out of service due to an abnormal AC system or fault, the converter station operator shall immediately report the disturbance to NPCC.

# Equipment Status Report (ESR) before start of commissioning tests:

Commissioning Directors at both Matiari and Lahore converter stations shall submit following ESR to NPCC prior to commissioning test each day as follows:

  - AC breakers controlling converter transformer of pole I and II at both Matiari/Lahore C/S are in cold standby state or otherwise.

  - Complete DC switchgear at Matiari/Lahore C/S is in *cold standby state.

  - DC line of pole I and II at both Matiari/Lahore C/S is in *cold standby state.

  - All AC filters at both Matiari/Lahore C/S are in “Ready for Operation” condition.

  - AC lines and the remaining 500 kV equipment at both Matiari/Lahore C/S is in normal operation.

# Commissioning Test Startup Procedure:

Commissioning Directors at both Matiari and Lahore converter stations shall seek a telephonic permission from NPCC, to formally start the tests as mentioned in the approved plan of that particular day after receiving the acknowledgement of “Commissioning Application” (as mentioned in 4.3) from NPCC. The prerequisites and Test steps related to each individual tests are described below:

# Initial Operation Tests, Joint Power Control, Normal Power Direction, Bi-Pole Ground Return

Follow the sequence described in “Annexure-D-I” and “Test Plan (A4).

# Pole Compensation, Joint Power Control, Normal Power Direction, Bi-Pole Ground Return

Follow the sequence described in “Annexure-D-II” and “Test Plan (A4).

# Automatic Power Curve Control Test, Joint Power Control, Bi-Pole Ground Return

Follow the sequence described in “Annexure-D-III” and “Test Plan (A4).

# Normal/Reduced Voltage Operation, Joint Power Control, Bi-Pole Ground Return

Follow the sequence described in “Annexure-D-IV” and “Test Plan (A4).

# Backup Control, Joint Power Control, Bi-Pole Ground Return

Follow the sequence described in “Annexure-D-V” and “Test Plan (A4).

# Pole Compensation by Disturbance tests, Joint Power Control, Normal Power Direction, Bi-Pole Ground Return

Follow the sequence described in “Annexure-D-VI” and “Test Plan (A4).

# Operation with Station Ground Test, Joint Power Control, Normal Power Direction, Bi-Pole Ground Return

Follow the sequence described in “Annexure-D-VII” and “Test Plan (A4).

# Disturbances, Joint Power Control, Bi-Pole Ground Return

Follow the sequence described in “Annexure-D-VIII” and “Test Plan (A4).

# Frequency Control Test, Joint Power Control, Bi-Pole Ground Return

Follow the sequence described in “Annexure-D-IX” and “Test Plan (A4).

# Initial Operation Tests, Bi-Pole Ground Return Operation, Reversed Power Direction, Joint Power Control

Follow the sequence described in “Annexure-D-X” and “Test Plan (A4).

# Protective Trip X, Y, and Z, Reversed Power Direction, Joint Power Control, Normal Power Direction, Bi-Pole Ground Return

Follow the sequence described in “Annexure-D-XI” and “Test Plan (A4).

# Pole Compensation and disturbance test, Reversed Power Direction, Joint Power Control, Bi-Pole Ground Return

Follow the sequence described in “Annexure-D-XII” and “Test Plan (A4).

# AC/DC Line Faults, Joint Power Control, Bi-Pole Ground Return

Follow the sequence described in “Annexure-D-XIII” and “Test Plan (A4).