## Slide 1: PMLTC Converter Transformer Protection

## Slide 2: LV Reactor Control Strategy at Matiari Side
All the LV Reactors always participate in the “converter bus voltage control” instead of “converter station reactive power control “ before and after DC deblocking.
At an AC voltage of higher than 532KV, 1 LV reactor bank is connected with a delay of 5s and the selection principle of such a bank is to make the LV reactors tend to be balanced under two tie-in transformers, while the LV reactors participating in reactive power balance of the converter stations do not participate in voltage control. At an AC voltage of lower than 488KV, one LV reactors is disconnected with a delay of 5s and the selection principle of such a reactor is to make the LV reactors tend to be balanced under two tie-in transformers. The LV reactors participate in reactive power balance of the converter stations do not participate in voltage control.

## Slide 3: LV Reactor Control Strategy at Lahore Side
At an AC voltage of higher than 532KV, 1 LV reactor bank is connected with a delay of 5s and the selection principle of such a bank is to make the LV reactors tend to be balanced under two tie-in transformers, while the LV reactors participating in reactive power balance of the converter stations do not participate in voltage control. At an AC voltage of lower than 488KV, one LV reactors is disconnected with a delay of 5s and the selection principle of such a reactor is to make the LV reactors tend to be balanced under two tie-in transformers. The LV reactors participate in reactive power balance of the converter stations do not participate in voltage control.

## Slide 4: Control Modes
The reactive power control of Mitiari and Lahore Converter Station has the following modes:
1)On Mode 2) Manual Mode
3)Automatic Mode 4) Off Mode
1. On Mode :-
If the reactive power control is in ON mode , the system automatically activates the manual mode. In this case, operators can select the automatic mode.
2. Manual Mode :-
If the reactive power control is in manual mode, only the connecting/ disconnecting of filters with high priority is automatically completed by reactive Power Control. The connecting/disconnecting of filters with high priority includes:
Over voltage control
Abs Min Filter
Umax
Qmax

## Slide 5
Control Modes
There are four control modes for QPC including on mode, manual mode, automatic mode and off mode.
3. Automatic mode:
Operator set the relevant reference value
Connecting and disconnecting of filters is automatically completed by QPC
4. Off Mode
This mode can be manually selected
Automatic performance operation of QPC is locked
Operator can perform connecting/disconnecting operation manually
Other Functions of QPC
According to current operating condition and status of filters QPC can determine the number of filter to be connected or disconnected

## Slide 6
Filter banks of the same type are connected in cyclic manner
During power run up/back process ,the connecting and disconnecting of filters shall follow the certain sequence
Replacement of filter (in result of protection action) is done according to the requirement of abs min or min filters: if trip belong to abs min and min filter, another filter is connected with in 0.5 and 5 seconds respectively.
QPC obtain the information of AC switch yard from station control system as:
  Filters that have been connected
  Filter banks that have been disconnected
  Filter banks that can be connected
A filter banks is considered unavailable if it fails to response in a certain period of time
After disconnection of filter bank, it should be discharged for a certain period of time

## Slide 7
Anti-oscillation measures:
This function measures the connecting/disconnecting time of filter. If connecting/disconnecting time exceeds a certain value, RPC automatically switches to manual control mode.
Reactive power equipment:
Total reactive power capacity of LCS is 2480 MVAR. There are total 4 banks which is further divided into 16 sub-banks.
Alarm and Events:
Following function cause SER that are sent to SCADA:
Selection and switching of manual/automatic control mode.
Selection and switching of u control/Q control mode.
Failure to satisfy the condition of Min. filter
Oscillation due to repeated connecting/disconnecting of filter bank.
Power drop due to failure to satisfy the condition of Abs Min Filter.
Measurement of Reactive Power and AC bus voltage:
The reactive power of sub-bank is directly measure by measuring “Sub-bank current” and “Bank Voltage” from CT/PT. Reactive power is measured and calculated through DFU-420.

## Slide 8: Selection and Switching of Control Position
The switching of control position of each functional group:
System Level
Station Level
is completed separately in DC station control with position status sent to pole control system.
Request-release logic
The master control position is selected by request-release logic. Switching is executed only if a request is received from other control positions. Master control position must be released within 60 seconds, otherwise the request is considered invalid.
If the request is for a remote dispatching center control position, the control position can be switched directly without release so that operators can take over control any time.
In case of DC station control system LAN communication fault and communication fault between workstations at effective control positions, control positions are set to an undefined status, SER alarm of respective functional group is generated and the control can be handed over directly without release if there is a request.

## Slide 9: Selection and switching of Control Level
The system control level can be switched in the master control system of any station provided that:
DC Station Control Communication is normal: LAN connected to DC Station Control of other station and LAN connected to an effective system control position.
Pole 1/2 Control Communication is normal: IFC communication connected to DC Station Control and LAN connected to an effective system control position.
The DC station control receives switching orders from other station. The actual control level is sent to the pole control system for switching of settings and to the HMI system for display.
Master/ Slave stations are allocated by station control software through request/ release logic. The slave station can request to act as master station at any time, but the master must release control within 60 seconds of the request for the successful transfer of master station functions.

## Slide 10: Data exchange with DC Station Control of the other Station
Data between Station is realized with LAN1 and LAN2 through LAN/WAN conversion by data router.
Inter-station Communication is divided into two types
Slow type:
A slow type communication is the data transfer of pole control, operator workstation through DC station control.
Fast Type:
If two sets of pole control of relate station fail, a pole control ESOF signal of related station is transmitted to DC station of other station through fast interstation communication.
In case of communication faults between 2 stations all the data that have been transferred to other station marked as invalid using ‘invalid bit’
DC station control handles the events transmitted by I/O unit through fieldbus and those generated by DC station control application software. These functions are implemented in HCM3000 application software
Sequence of Events Recording

## Slide 11
Monitoring Logic and System switching
Operation status is monitored through hardware, software & background monitoring. Hardware monitoring is to determine the fault by observing panels LED and instrument clusters. Software monitoring is to determine the cause of fault through application software from station control system. Background monitoring is to determine the fault information through background communication status, software fault, software alarm lamp status and relevant SER.
DC station control system has two switching modes i.e., software switching and hardware switching. If the fault system of slave system is higher than master system through comparison of fault level of redundant systems, software switching is activated. Hardware switching is mainly a result of hardware fault of cabinet, board and fan lamp. If the switching device of master system receives a “hardware not OK” signal of the related system, then this system is marked as slave and a hard contact signal is transmitted to the switching device of redundant systems, to switch the slave system of the redundant systems to the master system.

## Slide 12: Redundancy function
The DC station control system uses HCM3000 hardware with 2 panels, 2 field bus board(with one of each act as redundant) , connected through field bus for communication with redundant local measurement and control devices DFU420. Each system has two LAN Boards for cross commuincation with HMI/RCI and control system. The two redundant control systems exchange data through IFC control bus.
Data received from the slave system is compared with the corresponding data of the related system. If these data are consistent, it is considered valid and used to refresh the corresponding data of the related system.
Only the operation orders received by the master system of DC station are considered valid, and the master system of DC station control finally issues an order request to the I/O unit for control after processing these orders. The field equipment monitoring signals received and processed by the master and slave systems of DC station are considered valid and finally uploaded to LAN for processing in the HMI system.

## Slide 13: Description of Hardware
It consists of station control Panel A & panel B and each panel has HCM3000
Each powered by two DC220V supplies
DC220V/DC24V module gives DC24V for Switching logic
In case of power supply failure RED light is there which is powered by AC220V
HCM300 control cabinet further has 3 EPU20B CPU Boards
Functions of 3 EPU20B are:
  first is for communication processing and Reactive power control
  Second is for DC switchyard sequence control and DC switchyard control and monitoring
  third is for external fault recorder communication
ViGET is software used in HCM3000

## Slide 14: Software Description
The DC station control system is realized by the system of the control and protection platform HCM 3000
The development tool that is used is ViGET
ViGET is an integrated graphical application software development environment can it provide the functions such as engineering project creation, hardware configuration, communication configuration, graphical CFC program editing and downloading and on-line debugging.
DC station control system has different function packs. These functions are processed by two processors CPU1 and CPU2

## Slide 15: Interface
Terminal connection mode is used in the design of interfaces with DC system control
Two kind of terminals:
Power Supply Terminal
Control Circuit Terminal
Special plug connectors are used for the LAN and fieldbus connections.
LAN: Two way communication between DC station control system and DC system is done with the interface in LAN and passive contact form.
Clock Synchronization: Both Matiari and Lahore converter stations are equipped with dual station master clock systems with GPS. Protection and control system of the station synchronizes with the clock system in form of B code.

## Slide 16: Interface with safety stability system
Safety stability system regulates the DC system power by means of continuous analog monitoring.
This system output following signals to the DC station Control:
Power Run Up
Power Run Back
Blocking DC Signals
While DC system output following signals to the safety stability system:
Operating status of pole control
  Bipole power mode
  Monopolar power mode
Abnormal Trip Signals of Double Poles
Diagnose Interface: LAN ports on each CPU board can be used as program diagnosis ports. Online diagnostic debugging can be done by setting IP address in the program and downloading the program into the concerned CPU board.

## Slide 17: Subsystem Monitoring and Indication
Hardware Monitoring function
Power Supply Monitoring:
In case of Power failure, the red alarm lamp on the top of the cubicle is on.
Host Hardware Fault Monitoring:
There is an LED indicator lamp on the host board to indicate fault diagnosis of the board.
1. Self-test and monitoring of ECM10A Board:
In the front of Panel there are 6 Interfaces (X1 - X6) and 6 LED Indicator Lamps (H1 – H6).
Operating and Fault Status = H1 and H2
Operating status of two PROFIBUS DP Interfaces = H3 and H4
Operating Status of two CAN Interfaces = H5 and H6
2. Self-test and monitoring of ENT10B Board :
In the front of Panel there are 4 Interfaces (X2 – X5) and 6 LED indicator Lamps (H1-H6)
Operating and Fault Status = H1 and H2
Operating Status of four Ethernet Interfaces = H3,H4,H5 and H6

## Slide 18: Subsystem Monitoring and Indication
3. Self-test and monitoring of ESP10C Board:
This board performs the following functions:
i. Fault Diagnosis
ii. Fault Information Collection
iii. LED Display of Fault Content
Self test error of Channel 9 during initialization will cause LED A to display.
Error in reading calibration will cause LED C to display.
AD self test status error will display No LED.
Self test error occurring for three consecutive times will cause LED E to display.
FPGA Loading failure of ESP will cause LED F to displays.
When CPU detects a fault above ESP, It will give alarm to OWS. When Faults A and F are detected, system switching is effected.