## Intro
Bipole Low Power Tests Dispatch Matrices
All these tests will be performed in Bipolar Mode.
Sequence as mentioned in sequence table shall be followed
General conditions and System configurations must be selected as indicated before performing each test.
There are four voltage reactors available at Matiari and two LV reactors available at Lahore converter station.

## Test Sequence
Matiari—Lahore ±660kV HVDC Project The Schedule for Bipole System Commissioning Tests
Sr. No. | Test Block | Commissioning Items | Mode | Item Designations | Sub-item Designation | Power imported from AC Network
(MW)
Bipole Low Power System Test
All tests above must be sucessful before executing these tests
All tests in LP 12,13,14,15 should be performed in sequence. May not proceed with suceeding tests within the block other than ramping tests if any test in the block fails. May not proceed with following block tests until each test block is complete.
Bipole Low Power Operational Tests
1 | LP-12 | 2.3.1 | BPGR | Initial Operation Tests, Normal Power Direction | Start/Stop Pole, Manual Deblock/Block | 400
2 |  | 3.3.1 | BPGR | Pole Compensation | Normal Power Direction, Bipolar Power Ramping | 800
3 |  | 3.3.2 | BPGR | Pole Compensation | Normal Power Direction, Bipole Operation, Pole 2 Power Ramping | 800
4 |  | 3.3.3 | BPGR | Pole Compensation | Normal Power Direction, Bipole Operation, Pole 1 Power Ramping | 800
5 |  | 7.3.1 | BPGR | Automatic Power Curve Control Test | Automatic Power Curve Control test in Matiari Converter Station | 600
6 |  | 7.3.2 | BPGR | Automatic Power Curve Control Test | Automatic Power Curve Control test in Lahore Converter Station | 600
7 |  | 5.3.1 | BPGR | Reduced Voltage Operation | Reduced Voltage Operation Test | 600
8 |  | 9.3.1 | BPGR | Backup Control | Bipole Start/Stop in Backup Panel at Matiari | 400
9 |  | 9.3.1 | BPGR | Backup Control | Bipole Start/Stop in Backup Panel at Lahore | 400
10 |  | 9.3.2 | BPGR | Backup Control | Bipole Ramp up/down in Backup Panel | 600
Bipole Low Power Disturbance Tests
11 | LP-13 | 3.3.4 | BPGR | Pole Compensation by disturbance | Pole-2 Trip, Power Transfer at Normal Voltage | 800
12 |  | 3.3.4 | BPGR | Pole Compensation by disturbance | Pole-1 Trip, Power Transfer at Normal Voltage | 800
13 |  | 3.3.5 | BPGR | Pole Compensation by disturbance | Pole-1 Trip, Power Transfer at Reduced Voltage | 800
14 |  | 3.3.5 | BPGR | Pole Compensation by disturbance | Pole-2 Trip, Power Transfer at Reduced Voltage | 800
15 |  | 4.3.1 | BPGR | Operation with Station Ground | Start/Stop Bipole with Station Grounding at Matiari & LAHORE Converter Station | 600
16 |  | 6.3.1 | BPGR | Disturbances | Pole Trip, Open Line Fault at Electrode at Lahore | 400
17 |  | 6.3.1 | BPGR | Disturbances | Pole Trip, Open Line Fault at Electrode at Matiari | 400
18 |  | 6.3.2 | BPGR | Disturbances | Pole-1 in Operation while Pole-2 Undergoing Open Line Test | 400
19 |  | 6.3.2 | BPGR | Disturbances | Pole-2 in Operation while Pole-1 Undergoing Open Line Test | 400
20 |  | 6.3.3 | BPGR | Disturbances | Bipole Operation, Simulate Electrode Line Unbalance Fault | 600
21 |  | 6.3.4 | BPGR | Disturbances | Simulation of IDNC CT Transmitter Power Source Fault | 400
22 |  | 6.3.5 | BPGR | Disturbances | AC Auxiliary Power 400 V Switchover | 400
23 |  | 8.3.1 | BPGR | Frequency Control Test | Frequency Control test in Matiari Converter Station | 500
24 |  | 8.3.2 | BPGR | Frequency Control Test | Frequency Control test in Lahore Converter Station | 500
Bipole Low Power Tests -Reverse Power Direction
25 | LP-14 | 10.3.1 | BPGR | Initial Operation Tests, Reversed Power Direction | Start/Stop Bipole | 400
26 |  | 10.3.2 | BPGR | Initial Operation Tests, Reversed Power Direction | Control System Switchover | 400
27 |  | 11.3.1 | BPGR | Protective Trip X, Y, and Z, Reversed Power Direction | Protective Trip X in Rectifier with Telecommunication | 400
28 |  | 11.3.2 | BPGR | Protective Trip X, Y, and Z, Reversed Power Direction | Protective Trip Y in Inverter with Telecommunication | 400
29 |  | 11.3.3 | BPGR | Protective Trip X, Y, and Z, Reversed Power Direction | Protective Trip Z in Rectifier with Telecommunication | 400
30 |  | 12.3.1 | BPGR | Pole Compensation and disturbance test, Reversed Power Direction | Bipole Power Ramping | 800
31 |  | 12.3.2 | BPGR | Pole Compensation and disturbance test, Reversed Power Direction | Bipole Operation, Pole 2 Power Ramping with/without Telecommunication | 600
32 |  | 12.3.2 | BPGR | Pole Compensation and disturbance test, Reversed Power Direction | Bipole Operation, Pole 1 Power Ramping with/without Telecommunication | 600
33 |  | 12.3.3 | BPGR | Pole Compensation and disturbance test, Reversed Power Direction | Simulated Pole1 DC Line Fault (only Lahore) | 400
34 |  | 12.3.4 | BPGR | Pole Compensation and disturbance test, Reversed Power Direction | Simulated Pole2 DC Line Fault (only Lahore) | 400
Bipole Low Power Tests -AC and DC Line Fault Tests
35 | LP-15 | 13.3.1 | BPGR | DC Line Faults | DC Line Faults at Pole 1 near Rectifier, Normal Power Direction | 400
36 |  | 13.3.2 | BPGR | DC Line Faults | Pole 2 Reduced Voltage, DC Line Faults at Pole 2 near Rectifier, Normal Power Direction | 400
37 |  | 13.3.3 | BPGR | DC Line Faults | DC Line Faults at Pole 1 near Inverter, Normal Power Direction | 400
38 |  | 13.3.4 | BPGR | DC Line Faults | Pole 1 Reduced Voltage, DC Line Faults at Pole 1 near Inverter, Normal Power Direction | 400
39 |  | 13.3.5 | BPGR | DC Line Faults | Pole 1 Reduced Voltage, DC Line Faults at Pole 2 near Inverter, Normal Power Direction | 400
40 |  | 13.3.6 | MR | DC Line Faults | DC Line Faults at Pole 2 near Inverter, Metallic Return Operation, Normal Power Direction | 200
41 |  | 13.3.4 | BPGR | DC Line Faults | Fault in Pole 2 at connection, with Pole-I running at 200 MW. | 400
42 |  | 13.3.5 | BPGR | DC Line Faults | DC Line Faults at Pole 1 near Rectifier, Reverse Power Direction | 400
43 |  | 13.3.6 | BPGR | DC Line Faults | DC Line Faults at Pole 2 near Inverter, Reverse Power Direction | 400
44 |  | 13.3.7 | BPGR | AC Line Faults | AC Line Faults at Rectifier, Normal Power Direction (Optional) | 400
45 |  | 13.3.8 | BPGR | AC Line Faults | AC Line Faults at Inverter, Normal Power Direction (Optional) | 400

## IOT, GR
Bipole Low Power Operational Tests
1-Initial Operation Tests, Joint Power Control, Normal Power Direction, Bi-Pole Ground Return.
Test Objective | The objective is to check the function of bipole deblock and block.
Condition | Sr. No. | Station | Action | Equipment/ Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side at Matiari C/S | Both Poles will operate in Bipole Ground Return Mode see Status Table "BP-GR" |  |  | BI-Pole Mode of Operation
| 4 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 5 |  | All the Prerequisites as mentioned in DC Dispatch Plan should be met.
| 6 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 7 |  | All electrical connections are available.
| 8 |  | Protection settings and protective circuits trip sequences tests must be completed.
| 9 |  | AC-switchyard and associated protections and sequences, including breaker failure protection, must be active.
| 10 |  | Correct grounding of all equipment is available.
| 11 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 12 |  | Thyristor valves and valve hall is cleaned.
| 13 |  | Converter transformers are demagnetized.
| 14 |  | Set tap changer to position giving lowest valve voltage
| 15 |  | Monopole Low Power Tests have been successfully completed.
| 16 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (400 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 17 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 18 |  | Return | Ground |  | Ground Return Mode
| 19 |  | Udc Mode | Normal |  | ±660kV
| 20 |  | Telecom Mode | Operational
| 21 |  | Master Station | Matiari
| 22 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 23 |  |  | B | Standby
| 24 |  | Pole Control (PCP) | A | ACTIVE
| 25 |  |  | B | Standby
| 26 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 27 |  | Station Control Mode | Joint | ACTIVE | Matiari & Lahore will operate jointly.
| 28 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 29 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Start/Stop Bi-Pole, Manual Deblock/Block (Sr. No. 1) (A4 2.3.1) | 30 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 31 | Matiari/Lahore C/S DC side | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 32 | Matiari | Start the BiPole | Power | 400 MW
| 33 |  |  | Ramp Rate: | 50MW/Min
| 34 |  | Wait to achieve Target Value | Max Time | 5 min
| 35 |  | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 36 |  |  | DC Voltages | ±660kV
| 37 |  |  | RPC Operation | BP-11/13 , HP24/36
| 38 | Lahore |  | Extinction Angle (g) | 17°
| 39 |  |  | DC Voltages | Range to be mentioned
|  |  |  | RPC Operation | 2xHP12/24
| 40 | Matiari/Lahore | Verify stable operation at minimum power.
| 41 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 42 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 43 | Lahore |  | HP-12/24, HP-12/24
| 44 | Matiari | Stop the BiPole
| 45 |  | Verify Performance parameters | Retard, Reduced Current |  | Block without BPP
| 46 | Lahore |  | Alpha angle | 90 | Block with BPP
Test Acceptance Criteria | 47 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 48 |  | All Operations executed successfully
| 49 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 50 |  | All thyristor check-back signals are available.
| 51 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 52 |  | Measuring quantities are available and the values are within the specified range and phase.
| 53 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 54 |  | No Stuck Condition
| 55 |  | No False Tripping by DC Protection System
| 56 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 57 |  | No Tripping in AC side of converter Station

## PC
Bipole Low Power Operational Tests
2-Pole Compensation Joint Power Control, Normal Power Direction, Bi-Pole Ground Return
Test Objective | The test objective is to check the pole compensation function.
Condition | Sr. No. | Station | Action | Equipment/ Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side at Matiari C/S | Both Poles will operate in Bipole Ground Return Mode see Status Table "BP-GR" |  |  | BI-Pole Mode of Operation
| 4 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 5 |  | All the Prerequisites as mentioned in DC Dispatch Plan should be met.
| 6 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 7 |  | All electrical connections are available.
| 8 |  | Protection settings and protective circuits trip sequences tests must be completed.
| 9 |  | AC-switchyard and associated protections and sequences, including breaker failure protection, must be active.
| 10 |  | Correct grounding of all equipment is available.
| 11 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 12 |  | Thyristor valves and valve hall is cleaned.
| 13 |  | Converter transformers are demagnetized.
| 14 |  | Set tap changer to position giving lowest valve voltage
| 15 |  | Initial Operation Tests, Normal Power Direction (Annex-D-I must be successful)
| 16 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (800 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 17 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 18 |  | Return | Ground |  | Ground Return Mode
| 19 |  | Udc Mode | Normal |  | ±660kV
| 20 |  | Telecom Mode | Operational
| 21 |  | Master Station | Matiari
| 22 | Configuration Setting at Matiari & Lahore C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 23 |  |  | B | Standby
| 24 |  | Pole Control (PCP) | A | ACTIVE
| 25 |  |  | B | Standby
| 26 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 27 |  | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 28 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 29 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Normal Power Direction, Bipolar Power Ramping (Sr. No. 2) (A4 3.3.1) | 30 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 31 |  | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 32 | Matiari | Start the BiPole | Power | 400 MW
| 33 |  |  | Ramp Rate: | 50MW/Min
| 34 |  | Wait to achieve Target Value | Max Time | 5 min
| 35 |  | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 36 |  |  | DC Voltages | ±660kV
| 37 |  |  | RPC Operation | BP-11/13 , HP24/36
| 38 | Lahore |  | Extinction Angle (g) | 17°
| 39 |  |  | DC Voltages | Range to be mentioned
| 40 |  |  | RPC Operation | 2xHP12/24
| 41 | Matiari/Lahore | Verify stable operation at minimum power
| 42 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 43 | Lahore |  | HP-12/24, HP-12/24
| 44 | Matiari | Ramp Up | 400 MW | 600 MW | 50 MW/min
| 45 |  | Verify (During Ramping) | PCP-A ,SC-A | ACTIVE
| 46 |  | Manual Switch Control System (During Ramping) | PCP-A to | PCP-B
| 47 |  |  | PCP-B to | PCP-A
| 48 |  |  | SC-A to | SC-B to
| 49 |  |  | SC-B to | SC-A to
| 50 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 51 |  |  | PCP-A & SC-A is active
| 52 |  |  | power reaches the reference value after ramping is completed
| 53 |  |  | No Transients or unexpected delays
| 54 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 200 MW with DC System. (Sudden load sharing from AC corridor to DC corridor will happen in next step)
| 55 | Matiari | Ramp Up | 600 MW | 800 MW | 999 MW/min
| 56 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 57 |  |  | power reaches the reference value after ramping is completed
| 58 |  |  | No Transients
| 59 | Matiari | Ramp Down | 800 MW | 600 MW | 50 MW/min
| 60 |  | Verify (During Ramping) | PCP-A & SC-A | ACTIVE
| 61 |  | Manual Switch Control System (During Ramping) | PCP-A to | PCP-B
| 62 |  |  | PCP-B to | PCP-A
| 63 |  |  | SC-A to | SC-B to
| 64 |  |  | SC-B to | SC-A to
| 65 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 66 |  |  | PCP-A & SC-A is active
| 67 |  |  | power reaches the reference value after ramping is completed
| 68 |  |  | No Transients or unexpected delays
| 69 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 200 MW with DC System. (Sudden load sharing from DC corridor to AC corridor will happen in next step)
| 70 | Matiari | Ramp Down | 600 MW | 400 MW | 999 MW/min
| 71 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 72 |  |  | power reaches the reference value after ramping is completed
| 73 |  |  | No Transients
| 75 | Matiari | Ramp Up | 400 MW | 800 MW | 50 MW/min
| 76 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 77 |  |  | power reaches the reference value after ramping is completed
| 78 |  |  | No Transients
Normal Power Direction, Bipole Operation, Pole 2 Power Ramping (Sr. No. 3) (A4 3.3.2) | 79 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 80 |  | Verify Pole-I and Pole-II is in stable Bi-Pole Power Control Mode at 800 MW in sequence to test above.
| 81 |  | Order Pole-2 in Pole Power Control Mode, (Pole-I is in Bi-Pole Power Control Mode)
| 82 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 83 |  |  | Pole Power Control Mode achieved successfully in Pole 2
| 84 |  |  | No Transients
| 85 |  | Order Pole-2 in Pole Current Control Mode, (Pole-I is in Bi-Pole Power Mode)
| 86 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 87 |  |  | Pole Current Control Mode achieved successfully in Pole 2
| 88 |  |  | No Transients
| 89 | Lahore | Initiate Sequence of Master Station
| 90 |  | Ramp Up Pole-2 | 606 Amps | 700 Amps | 50 Amps/Min
| 91 | Lahore | Verify (During Ramping) | PCP-A | ACTIVE
| 92 |  | Manual Switch Control System (During Ramping) | PCP-A to | PCP-B
| 93 |  |  | PCP-B to | PCP-A
| 94 |  |  | SC-A to | SC-B to
| 95 |  |  | SC-B to | SC-A to
| 96 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 97 |  |  | PCP-A & SC-A is active
| 98 |  |  | current reaches the reference value after ramping is completed
| 99 |  |  | No Transients
| 100 | Lahore | Ramp Up Pole-2 | 700 Amps | 800 Amps | 50 Amps/Min
| 101 |  | Order Pole-2 in Pole Power Control Mode, (Pole-I is in Bi-Pole Power Mode) during ramping
| 102 | Matiari /Lahore | Verify | No transfer to pole power control in pole 2 while ramping
| 103 |  |  | Continuous Steady Operation of the transmission
| 104 |  |  | current reaches the reference value after ramping is completed
| 105 |  |  | No Transients
| 106 | Matiari | Initiate Sequence of Master Station
| 107 |  | Ramp Down Pole-2 | 800 Amps | 700 Amps | 50 Amps/Min
| 108 | Matiari | Verify (During Ramping) | PCP-A | ACTIVE
| 109 |  | Manual Switch Control System (During Ramping) | PCP-A to | PCP-B
| 110 |  |  | PCP-B to | PCP-A
| 111 |  |  | SC-A to | SC-B to
| 112 |  |  | SC-B to | SC-A to
| 113 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 114 |  |  | PCP-A is active
| 115 |  |  | current reaches the reference value after ramping is completed
| 116 |  |  | No Transients
| 117 | Matiari | Ramp Up Pole-2 | 700 Amps | 606 Amps | 50 Amps/Min
| 118 |  | Disable the telecommunication in both channels during the ramping process.
| 119 | Matiari /Lahore | Verify | The Emergency Current Control mode would be automatically activated.
| 120 |  |  | The ramping of pole2 would be continued at a reduced ramp rate， and the current reference value would be reached when the telecommunication is disabled,
| 121 |  |  | No Transients
| 122 |  | Verify Two poles are in stable operation at 800MW.
| 123 | Matiari | Enable the telecommunication in both channels.
| 124 |  | order pole 2 in Bipolar Power Control Mode
Normal Power Direction, Bipole Operation, Pole 1 Power Ramping (Sr. No. 4) (A4 3.3.3) | 125 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 126 |  | Verify Pole-I and Pole-II is in stable Bi-Pole Power Control Mode at 800 MW in sequence to test above.
| 127 |  | Order Pole-1 in Pole Power Control Mode, (Pole-2 is in Bi-Pole Mode)
| 128 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 129 |  |  | Pole Power Control Mode achieved successfully in Pole 1
| 130 |  |  | No Transients
| 131 |  | Order Pole-1 in Pole Current Control Mode, (Pole-2 is in Bi-Pole Power Mode)
| 132 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 133 |  |  | Pole Current Control Mode achieved successfully in Pole 1
| 134 |  |  | No Transients
| 135 | Lahore | Initiate Sequence of Master Station
| 136 |  | Ramp Up Pole 1 | 606 Amps | 700 Amps | 50 Amps/Min
| 137 |  | Verify (During Ramping) | PCP-A | ACTIVE
| 138 |  | Manual Switch Control System (During Ramping) | PCP-A to | PCP-B
| 139 |  |  | PCP-B to | PCP-A
| 140 |  |  | SC-A to | SC-B to
| 141 |  |  | SC-B to | SC-A to
| 142 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 143 |  |  | PCP-A & SC-A is active
| 144 |  |  | current reaches the reference value after ramping is completed
| 145 |  |  | No Transients
| 146 | Lahore | Ramp Up Pole 1 | 700 Amps | 800 Amps | 50 Amps/Min
| 147 |  | Order Pole-1 in Pole Power Control Mode, (Pole-2 is in Bi-Pole Power Mode) during ramping
| 148 | Matiari /Lahore | Verify | No transfer to pole power control in pole 1 while ramping
| 149 |  |  | Continuous Steady Operation of the transmission
| 150 |  |  | current reaches the reference value after ramping is completed
| 151 |  |  | No Transients
| 152 | Matiari | Initiate Sequence of Master Station
| 153 |  | Ramp Down Pole 1 | 800 Amps | 700 Amps | 50 Amps/Min
| 154 | Matiari | Verify (During Ramping) | PCP-A & SC-A | ACTIVE
| 155 |  | Manual Switch Control System (During Ramping) | PCP-A to | PCP-B
| 156 |  |  | PCP-B to | PCP-A
| 157 |  |  | SC-A to | SC-B to
| 158 |  |  | SC-B to | SC-A to
| 159 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 160 |  |  | PCP-A & SC-A is active
| 161 |  |  | current reaches the reference value after ramping is completed
| 162 |  |  | No Transients
| 163 | Matiari | Ramp Down Pole 1 | 700 Amps | 606 Amps | 50 Amps/Min
| 164 |  | Disable the telecommunication in both channels during the ramping process.
| 165 | Matiari /Lahore | Verify | The Emergency Current Control mode would be automatically activated.
| 166 |  |  | current reaches the reference value after ramping is completed
| 167 |  |  | No Transients
| 168 |  | Verify Two poles are in stable operation at 800MW
| 169 | Matiari | Enable the telecommunication in both channels
| 170 |  | Order pole 1 in Bipolar Power Control Mode
Test Acceptance Criteria | 171 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 172 |  | All Operations executed successfully
| 173 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 174 |  | All thyristor check-back signals are available.
| 175 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 176 |  | Measuring quantities are available and the values are within the specified range and phase.
| 177 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 178 |  | No Stuck Condition
| 179 |  | No False Tripping by DC Protection System
| 180 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 181 |  | No Tripping in AC side of converter Station

## APC
Bipole Low Power Operational Tests
3-Automatic Power Curve Control Test Joint Power Control, Bi-Pole Ground Return
Test Objective | The test is to check the basic function of automatic power curve control of DC system.
Condition | Sr. No. | Station | Action | Equipment/ Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side at Matiari C/S | Both Poles will operate in Bipole Ground Return Mode see Status Table "BP-GR" |  |  | BI-Pole Mode of Operation
| 4 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 5 |  | All the Prerequisites as mentioned in DC Dispatch Plan should be met.
| 6 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 7 |  | All electrical connections are available.
| 8 |  | Protection settings and protective circuits trip sequences tests must be completed.
| 9 |  | AC-switchyard and associated protections and sequences, including breaker failure protection, must be active.
| 10 |  | Correct grounding of all equipment is available.
| 11 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 12 |  | Thyristor valves and valve hall is cleaned.
| 13 |  | Converter transformers are demagnetized.
| 14 |  | Air humidity and temperature in valve hall are within expected limits.
| 15 |  | Pole Compensation (Annex-D-II must be successful)
| 16 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (600 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 17 |  | OLT has been finished.
| 18 |  | Both sides of AC system is capable to supply the power for the test.
| 19 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 20 |  | Return | Ground |  | Ground Return Mode
| 21 |  | Udc Mode | Normal |  | ±660 kV
| 22 |  | Telecom Mode | Operational
| 23 |  | Master Station | Matiari
| 24 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 25 |  |  | B | Standby
| 26 |  | Pole Control Protection (PCP) | A | ACTIVE
| 27 |  |  | B | Standby
| 28 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 29 |  | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 30 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 31 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Automatic Power Curve Control test | 32 | Matiari | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 33 |  | Verify Matiari is Master Station.
| 34 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 35 | Matiari & Lahore | Start the BiPole | Power | 400 MW
| 36 |  |  | Ramp Rate: | 50 MW/Min
| 37 |  | Wait to achieve Target Value | Max Time | 5 min
| 38 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 39 |  |  | DC Voltages | ±660kV
| 40 |  |  | Electrode Current | <30 Amps
| 41 |  |  | RPC Operation | BP-11/13 , HP24/36
| 42 | Lahore |  | Extinction Angle (g) | 17°
| 43 |  |  | DC Voltages | Range to be mentioned
| 44 |  |  | RPC Operation | 2xHP12/24
| 45 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 46 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 47 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 48 | Lahore |  | 2xHP12/24
Automatic Power Curve Control test in Matiari Converter Station (Sr. No. 5) (A4 7.3.1) | 49 | Matiari | Set the bipole power curve and then switch the bipolar power control to automatic power control
| 50 |  | Bipole Automatic Power Curve Setting | Bipolar power 400MW lasts for 15 minutes.
| 51 |  |  | The power ramps up from 400MW to 500MW at a rate of 7MW/min.Manually switch the system during the power ramping up, including pole control and DC station control system.
| 52 |  |  | The bipolar power 500MW lasts for 30 minutes
| 53 |  |  | The power ramps up from 500MW to 600MW at a rate of 7MW/min.
| 54 |  |  | The bipolar power 600MW lasts for 30 minutes
| 55 |  |  | The power ramps down from 600MW to 500MW at a rate of 7MW/min.
| 56 |  |  | The bipolar power 500MW lasts for 30 minutes.
| 57 |  |  | The power ramps down from 500MW to 400MW at a rate of 7MW/min.
| 58 |  | During the power ramping down, click the "Hold" button on OWS to verify that the power stops ramping down. And switch the bipolar power control to manual power control.
| 59 |  | Manually ramp down the power to 400MW.
Automatic Power Curve Control test in Lahore Converter Station (Sr. No. 6) (A4 7.3.2) | 60 | Lahore | Initiate Master Sequence at Lahore Station
| 61 |  | Set the bipole power curve and then switch the bipolar power control to automatic power control
| 62 |  | BipolE Automatic Power Curve Setting | Bipolar power 400MW lasts for 15 minutes.
| 63 |  |  | The power ramps up from 400MW to 500MW at a rate of 7MW/min.Manually switch the system during the power ramping up, including pole control and DC station control system.
| 64 |  |  | The bipolar power 500MW lasts for 30 minutes
| 65 |  |  | The power ramps up from 500MW to 600MW at a rate of 7MW/min.
| 66 |  |  | The bipolar power 600MW lasts for 30 minutes
| 67 |  |  | The power ramps down from 600MW to 500MW at a rate of 7MW/min.
| 68 |  |  | The bipolar power 500MW lasts for 30 minutes.
| 69 |  |  | The power ramps down from 500MW to 400MW at a rate of 7MW/min.
| 70 |  | During the power ramping down, click the "Hold" button on OWS to verify that the power stops ramping down. And switch the bipolar power control to manual power control.
| 71 |  | Manually ramp down the power to 400MW.
Test Acceptance Criteria | 72 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 73 |  | All Operations executed successfully
| 74 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 75 |  | All thyristor check-back signals are available.
| 76 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 77 |  | Measuring quantities are available and the values are within the specified range and phase.
| 78 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 79 |  | No Stuck Condition
| 80 |  | No False Tripping by DC Protection System
| 81 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 82 |  | No Tripping in AC side of converter Station

## Reduced V Operations, P
Bipole Low Power Operational Tests
4-Normal/Reduced Voltage Operation Joint Power Control, Bi-Pole Ground Return
Test Objective | The test objective is to check the DC system performance during reduced voltage operation.
Condition | Sr. No. | Station | Action | Equipment/ Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side at Matiari C/S | Both Poles will operate in Bipole Ground Return Mode see Status Table "BP-GR" |  |  | BI-Pole Mode of Operation
| 4 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 5 |  | All the Prerequisites as mentioned in DC Dispatch Plan should be met.
| 6 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 7 |  | All electrical connections are available.
| 8 |  | Protection settings and protective circuits trip sequences tests must be completed.
| 9 |  | AC-switchyard and associated protections and sequences, including breaker failure protection, must be active.
| 10 |  | Correct grounding of all equipment is available.
| 11 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 12 |  | Thyristor valves and valve hall is cleaned.
| 13 |  | Converter transformers are demagnetized.
| 14 |  | Air humidity and temperature in valve hall are within expected limits.
| 15 |  | Automatic Power Curve Control Test (Annex-D-III must be successful)
| 16 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (600 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 17 |  | OLT has been finished.
| 18 |  | Both sides of AC system is capable to supply the power for the test.
| 19 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 20 |  | Return | Ground |  | Ground Return Mode
| 21 |  | Udc Mode | Reduced |  | ±462kV
| 22 |  | Telecom Mode | Operational
| 23 |  | Master Station | Matiari
| 24 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 25 |  |  | B | Standby
| 26 |  | Pole Control Protection (PCP) | A | ACTIVE
| 27 |  |  | B | Standby
| 28 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 29 |  | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 30 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 31 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Reduced Voltage Operation Test (Sr. No. 7) (A4 5.3.1) | 32 | Matiari | Set manually REDUCED VOLTAGE mode (70% of nominal voltage) in pole 1 from Matiari.
| 33 |  | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 34 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 35 | Matiari & Lahore | Start the Pole-1, | Power | 400 MW
| 36 |  |  | Ramp Rate: | 50 MW/Min
| 37 |  | Wait to achieve Target Value | Max Time | 5 min
| 38 | Matiari | Verify Performance indicators | Firing angle (α) | >15°±2.5° (expected pole 1), 15°±2.5° (pole 2), | Record the Firing angle and transformer tap
| 39 |  |  | DC Voltages (Pole-I) | 462 kV
| 40 |  |  | DC Voltages (Pole-II) | 660 kV
| 41 |  |  | Electrode Current | <30 Amps
| 42 |  |  | RPC Operation | BP-11/13 , HP24/36
| 43 | Lahore |  | Extinction Angle (g) | >17° (expected pole 1), 17° (pole 2) | Record the Firing angle and transformer tap
| 44 |  |  | DC Voltages | Range to be mentioned
| 45 |  |  | RPC Operation | 2xHP12/24
| 46 | Matiari & Lahore | Verify stable operation & Normal start at reduced with minimum power
| 47 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 48 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 49 | Lahore |  | 2xHP12/24
| 50 | Matiari | Order Reduced Voltages (462kV) in Pole-II
| 51 |  | Verify Pole 2 DC Voltages is ramping down to Reduced Voltages without change in power and reach the specified volatges smoothly and without any interruption.
| 52 | Matiari/Lahore | Verify | DC Voltages (Pole-I) | 462 kV | Record the Firing angle and transformer tap at both stations
| 53 |  |  | DC Voltages (Pole-II) | 462 kV | Record the Firing angle and transformer tap at both stations
| 54 |  |  | Electrode Current | <30 Amps
| 55 | Matiari | Ramp Up | 400 MW | 600 MW | 100 MW
| 56 | Matiari/Lahore | Verify DC Voltage remains unchanged as dc power ramps up and reaches the specified power smoothly and without any interruption.
| 57 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 200 MW with DC System. (Sudden load sharing from DC corridor to AC corridor will happen in next step)
| 58 |  | Ramp Down | 600 MW | 400 MW | 999 MW
| 59 | Matiari/Lahore | Verify DC Voltage remains unchanged as dc power ramps down quickly and reaches the specified power smoothly and without any interruption.
| 60 | Matiari/Lahore | Stop the Pole
| 61 |  | Verify Performance parameters | Retard, Reduced Current |  | Block without BPP
| 62 | Lahore |  | Alpha angle | 90 | Block with BPP
Test Acceptance Criteria | 63 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 64 |  | All Operations executed successfully
| 65 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 66 |  | All thyristor check-back signals are available.
| 67 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 68 |  | Measuring quantities are available and the values are within the specified range and phase.
| 69 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 70 |  | No Stuck Condition
| 71 |  | No False Tripping by DC Protection System
| 72 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 73 |  | No Tripping in AC side of converter Station

## BackUp Control
Bipole Low Power Operational Tests
5-Backup Control Joint Power Control, Bi-Pole Ground Return
Test Objective | The test is to check the deblock/block function from backup control.
Condition | Sr. No. | Station | Action | Equipment/ Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side at Matiari C/S | Both Poles will operate in Bipole Ground Return Mode see Status Table "BP-GR" |  |  | BI-Pole Mode of Operation
| 4 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 5 |  | All the Prerequisites as mentioned in DC Dispatch Plan should be met.
| 6 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 7 |  | All electrical connections are available.
| 8 |  | Protection settings and protective circuits trip sequences tests must be completed.
| 9 |  | AC-switchyard and associated protections and sequences, including breaker failure protection, must be active.
| 10 |  | Correct grounding of all equipment is available.
| 11 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 12 |  | Thyristor valves and valve hall is cleaned.
| 13 |  | Converter transformers are demagnetized.
| 14 |  | Air humidity and temperature in valve hall are within expected limits.
| 15 |  | Reduced Voltage Operation (Annex-D-IV must be successful)
| 16 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (600 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 17 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 18 |  | Return | Ground |  | Ground Return Mode
| 19 |  | Udc Mode | Normal |  | ±660 kV
| 20 |  | Telecom Mode | Operational
| 21 |  | Master Station | Matiari
| 22 | Configuration Setting at Matiari & Lahore C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 23 |  |  | B | Standby
| 24 |  | Pole Control Protection (PCP) | A | ACTIVE
| 25 |  |  | B | Standby
| 26 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 27 |  | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 28 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 29 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Bipole Start/Stop in Backup Panel at Matiari (Sr. No. 8) (A4 9.3.1) | 30 | Matiari | Switch DC Local Control Interface from ‘REMOTE’ to ‘LOCAL’.
| 31 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 32 | Matiari | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 33 |  | Start the BIPOLE | Power | 400 MW
| 34 |  |  | Ramp Rate: | 50 MW/Min
| 35 |  | Wait to achieve Target Value | Max Time | 5 min
| 36 |  | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 37 |  |  | DC Voltages | ±660kV
| 38 |  |  | RPC Operation | BP-11/13 , HP24/36
| 39 | Lahore |  | Extinction Angle (g) | 17°
| 40 |  |  | DC Voltages | Range to be mentioned
| 41 |  |  | RPC Operation | 2xHP12/24
| 42 | Matiari/Lahore | Verify stable operation & Normal start with minimum power
| 43 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 44 |  | normal start behavior and stable operation at minimum power
| 45 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 46 | Lahore |  | 2xHP12/24
| 47 | Matiari | Stop the Pole
| 48 |  | Verify Performance parameters | Retard, Reduced Current
| 49 | Lahore |  | Alpha angle | 90
| 50 | Matiari/Lahore | Verify normal stop behavior
| 51 | Matiari | Switch DC Local Control Interface from ‘LOCAL’ to ‘REMOTE’.
Bipole Start/Stop in Backup Panel at Lahore (Sr. No. 9) (A4 9.3.1) | 52 | Lahore | Switch DC Local Control Interface from ‘REMOTE’ to ‘LOCAL’.
| 53 |  | Initiate the sequence of MASTER station.
| 54 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 55 | Lahore | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 56 |  | Start the BIPOLE | Power | 400 MW
| 57 |  |  | Ramp Rate: | 50 MW/Min
| 58 |  | Wait to achieve Target Value | Max Time | 5 min
| 59 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 60 |  |  | DC Voltages | ±660kV
| 61 |  |  | RPC Operation | BP-11/13 , HP24/36
| 62 | Lahore |  | Extinction Angle (g) | 17°
| 63 |  |  | DC Voltages | Range to be mentioned
| 64 |  |  | RPC Operation | 2xHP12/24
| 65 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 66 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 67 |  | normal start behavior and stable operation at minimum power
| 68 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 69 | Lahore |  | 2xHP12/24
| 70 | Matiari | Stop the Pole
| 71 |  | Verify Performance parameters | Retard, Reduced Current
| 72 | Lahore |  | Alpha angle | 90
| 73 | Matiari/Lahore | Verify normal stop behavior
| 74 | Lahore | Confirm DC Local Control Interface is set to ‘LOCAL’
Bipole Ramp up/down in Backup Panel (Sr. No. 10) (A4 9.3.2) | 75 | Matiari | Switch DC Local Control Interface from ‘REMOTE’ to ‘LOCAL’.
| 76 |  | Initiate the sequence of MASTER station.
| 77 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 78 | Matiari & Lahore | Start the Bi-Pole | Power | 400 MW
| 79 |  |  | Ramp Rate: | 50 MW/Min
| 80 |  | Wait to achieve Target Value | Max Time | 5 min
| 81 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 82 |  |  | DC Voltages | ±660kV
| 83 |  |  | RPC Operation | BP-11/13 , HP24/36
| 84 | Lahore |  | Extinction Angle (g) | 17°
| 85 |  |  | DC Voltages | Range to be mentioned
| 86 |  |  | RPC Operation | 2xHP12/24
| 87 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 88 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 89 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 90 | Lahore |  | 2xHP12/24
| 91 | Matiari | Ramp Up | 400 MW | 500 MW | 50 MW/Min
| 92 |  | Verify that the current reaches the reference value after each ramping is completed in both stations and that the ramping process is smooth and without disturbances.
| 93 |  | Ramp Up | 500 MW | 600 MW | 25 MW/Min
| 94 |  | Order STOP RAMPING (During Ramping).
| 95 |  | Verify also that the ramp could stop while ramping and power reaches the reference value after each ramping is completed in both stations and that the ramping process is smooth and without disturbances.
| 96 | Lahore | Initiate the sequence of MASTER station.
| 97 |  | Ramp Down | 600 MW | 500 MW | 50 MW/Min
| 98 |  | Verify that the power reaches the reference value after each ramping is completed in both stations and that the ramping process is smooth and without disturbances.
| 99 |  | Ramp Down | 500 MW | 400 MW | 25 MW/Min
| 100 |  | Order STOP RAMPING (During Ramping).
| 101 |  | Verify also that the ramp could stop while ramping and power reaches the reference value after each ramping is completed in both stations and that the ramping process is smooth and without disturbances.
| 102 | Matiari/Lahore | Switch DC Local Control Interface from ‘LOCAL’ to 'REMOTE'.
| 103 | Matiari/Lahore | Stop the Bipole
| 104 |  | Verify Performance parameters | Retard, Reduced Current |  | Block without BPP
| 105 | Lahore |  | Alpha angle | 90 | Block with BPP
Test Acceptance Criteria | 106 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 107 |  | All Operations executed successfully
| 108 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 109 |  | All thyristor check-back signals are available.
| 110 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 111 |  | Measuring quantities are available and the values are within the specified range and phase.
| 112 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 113 |  | No Stuck Condition
| 114 |  | No False Tripping by DC Protection System
| 115 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 116 |  | No Tripping in AC side of converter Station

## PC (distur)
Bipole Low Power DisturbanceTests
6-Pole Compensation by Disturbance tests Joint Power Control, Normal Power Direction, Bi-Pole Ground Return
Test Objective | The test objective is to check the pole compensation function.
Condition | Sr. No. | Station | Action | Equipment/ Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side at Matiari C/S | Both Poles will operate in Bipole Ground Return Mode see Status Table "BP-GR" |  |  | BI-Pole Mode of Operation
| 4 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 5 |  | All the Prerequisites as mentioned in DC Dispatch Plan should be met.
| 6 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 7 |  | All electrical connections are available.
| 8 |  | Protection settings and protective circuits trip sequences tests must be completed.
| 9 |  | AC-switchyard and associated protections and sequences, including breaker failure protection, must be active.
| 10 |  | Correct grounding of all equipment is available.
| 11 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 12 |  | Thyristor valves and valve hall is cleaned.
| 13 |  | Converter transformers are demagnetized.
| 14 |  | Set tap changer to position giving lowest valve voltage
| 15 |  | Bipole Low Power Operational tests (Annex-D-I,II,III,IV,V must be successful)
| 16 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (800 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 17 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 18 |  | Return | Ground |  | Ground Return Mode
| 19 |  | Udc Mode | Normal |  | ±660kV
| 20 |  | Telecom Mode | Operational
| 21 |  | Master Station | Matiari
| 22 | Configuration Setting at Matiari & Lahore C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 23 |  |  | B | Standby
| 24 |  | Pole Control (PCP) | A | ACTIVE
| 25 |  |  | B | Standby
| 26 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 27 |  | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 28 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 29 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Pole-2 Trip, Power Transfer at Normal Voltage (Sr. No. 11) (A4 3.3.4) | 30 | Matiari/Lahore | Verify Pole-I and Pole-II is in stable Bi-Pole Power Control Mode at 800 MW in sequence to test above.
| 31 | Matiari | Verify Pole 2 valve cooling pump A is active
| 32 |  | Switch off the AC power supply for the pump A in the valve cooling system in pole 2
| 33 |  | Verify the pump B is put into operation.
| 34 |  | Restore the AC power supply for the pump A in the valve cooling system in pole 2.
| 35 |  | Switch off the AC power supply for the pump B in the valve cooling system in pole 2
| 36 |  | Verify the pump A is put into operation.
| 37 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 38 | Matiari | Switch off the AC power supply for the pump A in the valve cooling system to simulate Valve Cooling System Fault in Matiari in pole 2.
| 39 |  | Verify Protection Functions | Y-block
| 40 |  |  | Trip | Converter T/F AC Breakers pole-2
| 41 |  |  | Pole IsolationSequence
| 42 |  |  | Start Breaker Failure Protection
| 43 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 44 | Lahore |  | Normal Y-stop sequence
| 45 | Matiari/Lahore |  | No influence on Transmissted power
| 46 | Matiari | Restore the AC power supply for the pumps A & B in the valve cooling system in pole 2.
| 47 | Lahore | De-energize the converter transformer at pole 2 in LAHORE station.
| 48 | Matiari/Lahore | Energize the converter transformer of pole 2.
| 49 | Matiari/Lahore | Verify that energization of converter transformer does not result in commutation failure on Pole 1 and has no influence on the transmitted bipole power.
| 50 | Matiari/Lahore | Order pole 2 in Pole Power Control.
| 51 | Matiari | Start Pole 2 | Power | 200 MW
| 52 |  |  | Ramp Rate: | 50MW/Min
| 53 | Matiari/Lahore | Order pole 2 in Bipolar Power Control Model.
| 54 | Matiari/Lahore | Verify | the power of pole 2 will rapidly ramp to 400MW for sharing the bipole power.
| 55 |  |  | there is no influence on the transmitted bipole power.
| 56 |  |  | Right RPC ACTION
Pole-1 Trip, Power Transfer at Normal Voltage (Sr. No. 12) (A4 3.3.4) | 57 | Matiari/Lahore | Verify Pole-I and Pole-II is in stable Bi-Pole Power Control Mode at 800 MW in sequence to test above.
| 58 | Matiari | Verify pole 1 valve cooling pump A is active
| 59 |  | Switch off the AC power supply for the pump A in the valve cooling system in pole 1
| 60 |  | Verify the pump B is put into operation.
| 61 |  | Restore the AC power supply for the pump A in the valve cooling system in pole 1
| 62 |  | Switch off the AC power supply for the pump B in the valve cooling system in pole 1
| 63 |  | Verify the pump A is put into operation.
| 64 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 65 | Matiari | Switch off the AC power supply for the pump A in the valve cooling system to simulate Valve Cooling System Fault in Matiari in pole 1
| 66 |  | Verify Protection Functions | Y-block
| 67 |  |  | Trip | Converter T/F AC Breakers pole-1
| 68 |  |  | Pole IsolationSequence
| 69 |  |  | Start Breaker Failure Protection
| 70 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 71 | Lahore |  | Normal Y-stop sequence
| 72 | Matiari/Lahore |  | No influence on Transmissted power
| 73 | Matiari | Restore the AC power supply for the pumps A & B in the valve cooling system in pole 1.
| 74 | Lahore | De-energize the converter transformer at pole 1 in LAHORE station.
| 75 | Matiari/Lahore | Energize the converter transformer of pole 1
| 76 | Matiari/Lahore | Verify that energization of converter transformer does not result in commutation failure on Pole 1 and has no influence on the transmitted bipole power.
| 77 | Matiari/Lahore | Order pole 1 in Pole Power Control.
| 78 | Matiari | Start Pole 1 | Power | 200 MW
| 79 |  |  | Ramp Rate: | 50MW/Min
| 80 | Matiari/Lahore | Order pole 1 in Bipolar Power Control Model.
| 81 | Matiari/Lahore | Verify | the power of pole 1 will rapidly ramp to 400MW for sharing the bipole power.
| 82 |  |  | there is no influence on the transmitted bipole power.
| 83 |  |  | Right RPC ACTION
Pole-1 Trip, Power Transfer at Reduced Voltage (Sr. No. 13) (A4 3.3.4) | 84 | Matiari/Lahore | Verify Pole-I and Pole-II is in stable Bi-Pole Power Control Mode at 800 MW in sequence to test above.
| 85 | Matiari | Order pole 2 in REDUCED VOLTAGE (70% of nominal voltage).
| 86 |  | Verify | order of pole 2 changed to reduced voltage successfully.
| 87 |  |  | there is no influence on the transmitted bipole power.
| 88 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 89 | Lahore | Simulate pole-I Pole Bus Differential Protection Stage 2TRIP
| 90 |  | Verify | Z-block
| 91 |  |  | Blocking of the converter with by-pass pair
| 92 |  |  | Trip Action | Converter T/F AC Breakers of Pole-I
| 93 |  |  | Pole IsolationSequence
| 94 |  |  | Start Breaker Failure Protection
| 95 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 96 | Matiari |  | Normal Y-stop sequence.
| 97 | Matiari/Lahore |  | there is no influence on the transmitted bipolar power and the HVDC system is still in operation.
| 98 | Matiari/Lahore | Switch pole 1 into Pole Power Control mode.
| 99 | Matiari | Start Pole 1 | Power | 200 MW
| 100 |  |  | Ramp Rate: | 50MW/Min
| 101 | Matiari/Lahore | Switch pole 1 into Bipolar Power Control Model mode.
| 102 | Matiari/ Lahore | Verify | power of pole 1 would rapidly boost to 470MW for sharing the bipole power and ensuring electrode balancing.
| 103 |  |  | there is no influence on the transmitted bipole power.
| 104 |  | Order pole 2 in Normal VOLTAGE.
| 105 |  | Verify that each pole is operating at 400MW (Bipole=800 MW)
Pole-2 Trip, Power Transfer at Reduced Voltage (Sr. No. 14) (A4 3.3.5) | 106 | Matiari/Lahore | Verify Pole-I and Pole-II is in stable Bi-Pole Power Control Mode at 800 MW in sequence to test above.
| 107 | Matiari | Order pole 1 in REDUCED VOLTAGE (70% of nominal voltage).
| 108 |  | Verify | order of pole 1 changed to reduced voltage successfully.
| 109 |  |  | there is no influence on the transmitted bipole power.
| 110 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 111 | Lahore | Simulate pole-2 Pole Bus Differential Protection Stage 2TRIP
| 112 |  | Verify | Z-block
| 113 |  |  | Blocking of the converter with by-pass pair
| 114 |  |  | Trip Action | Converter T/F AC Breakers of Pole-I
| 115 |  |  | Pole IsolationSequence
| 116 |  |  | Start Breaker Failure Protection
| 117 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 118 | Matiari |  | Normal Y-stop sequence.
| 119 | Matiari/Lahore |  | there is no influence on the transmitted bipolar power and the HVDC system is still in operation.
| 120 | Matiari/Lahore | Switch pole 2 into Pole Power Control mode.
| 121 | Matiari | Start Pole 2 | Power | 200 MW
| 122 |  |  | Ramp Rate: | 50MW/Min
| 123 | Matiari/Lahore | Switch pole 2 into Bipolar Power Control Model mode.
| 124 |  | Verify | power of pole 2 would rapidly boost to 470MW for sharing the bipole power and ensuring electrode balancing.
| 125 |  |  | there is no influence on the transmitted bipole power.
| 126 | Matiari | Order pole 1 in Normal VOLTAGE.
| 127 |  | Verify that each pole is operating at 400MW (Bipole=800 MW)
| 128 |  | Ramp Down | 800 MW | 400 MW | 50 MW/min
Test Acceptance Criteria | 129 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 130 |  | All Operations executed successfully
| 131 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 132 |  | All thyristor check-back signals are available.
| 133 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 134 |  | Measuring quantities are available and the values are within the specified range and phase.
| 135 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 136 |  | No Stuck Condition
| 137 |  | No False Tripping by DC Protection System
| 138 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 139 |  | No Tripping in AC side of converter Station

## OSG
Bipole Low Power DisturbanceTests
7-Operation with Station Ground Test Joint Power Control, Normal Power Direction, Bi-Pole Ground Return
Test Objective | The test objective is to check the function of electrode line balancing.
Condition | Sr. No. | Station | Action | Equipment/ Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side at Matiari C/S | Both Poles will operate in Bipole Ground Return Mode see Status Table "BP-GR" |  |  | BI-Pole Mode of Operation
| 4 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 5 |  | All the Prerequisites as mentioned in DC Dispatch Plan should be met.
| 6 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 7 |  | All electrical connections are available.
| 8 |  | Protection settings and protective circuits trip sequences tests must be completed.
| 9 |  | AC-switchyard and associated protections and sequences, including breaker failure protection, must be active.
| 10 |  | Correct grounding of all equipment is available.
| 11 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 12 |  | Thyristor valves and valve hall is cleaned.
| 13 |  | Converter transformers are demagnetized.
| 14 |  | Air humidity and temperature in valve hall are within expected limits.
| 15 |  | Pole Compensation by disturbance (Annex-D-VI must be successful)
| 16 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (600 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 17 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 18 |  | Return | Ground |  | Ground Return Mode
| 19 |  | Udc Mode | Normal |  | ±660kV
| 20 |  | Telecom Mode | Operational
| 21 |  | Master Station | Matiari
| 22 | Configuration Setting at Matiari & Lahore C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 23 |  |  | B | Standby
| 24 |  | Pole Control Protection (PCP) | A | ACTIVE
| 25 |  |  | B | Standby
| 26 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 27 |  | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 28 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 29 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Start/Stop Bipole with Station Grounding at Matiari & LAHORE Converter (Sr. No. 15) (A4 4.3.1) | 30 | Matiari/Lahore C/S DC side | Verify Poles are Blocked and qualify Ready for Operation Conditions.
| 31 | Matiari | Instruct to Close NGBS (Manually) | NGBS | Closed
| 32 |  | Instruct to Open MRTB (Manually) | MRTB | OPEN | now Matiari is at station grounding.
| 33 | Lahore | Instruct to Close NGBS (Manually) | NGBS | Closed
| 34 |  | Instruct to Open WN3Q11 (Manually) | WN3Q11 | OPEN | now Matiari is at station grounding.
| 35 | Matiari/ Lahore | Verify Pole 1 and Pole 2 in Bipolar Power Control Mode respectively
| 36 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing for upto 600 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 37 | Matiari | Start the BiPole | Power | 400 MW
| 38 |  |  | Ramp Rate: | 50MW/Min
| 39 |  | Wait to achieve Target Value | Max Time | 5 min
| 40 |  | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 41 |  |  | DC Voltages | ±660kV
| 42 |  |  | RPC Operation | BP-11/13 , HP24/36
| 43 | Lahore |  | Extinction Angle (g) | 17°
| 44 |  |  | DC Voltages | Range to be mentioned
| 45 |  |  | RPC Operation | 2xHP12/24
| 46 | Matiari/Lahore | Verify stable operation at minimum power.
| 47 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 48 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 49 | Lahore |  | HP-12/24, HP-12/24
| 50 | Matiari | Ramp Up | 400 MW | 600 MW | 50 Amps/Min
| 51 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 52 |  |  | current reaches the reference value after ramping is completed
| 53 |  |  | NBGS current<30 A
| 54 |  |  | No Transients
| 55 | Matiari | Ramp Down | 600 MW | 400 MW | 50 Amps/Min
| 56 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 57 |  |  | current reaches the reference value after ramping is completed
| 58 |  |  | NBGS current<30 A
| 59 |  |  | No Transients
| 60 | Matiari | Stop the Bipole
| 61 |  | Verify Performance parameters | Retard, Reduced Current |  | Block without BPP
| 62 | Lahore |  | Alpha angle | 90 | Block with BPP
| 63 | Matiari | Instruct to Close MRTB (Manually) | MRTB | Close
| 64 | Lahore | Instruct to Close WN3Q11 (Manually) | WN3Q11 | Close
| 65 | Matiari/Lahore | Instruct to Open NGBS (Manually) | NBGS | OPEN | Now both stations in ground return configuration
Test Acceptance Criteria | 66 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 67 |  | All Operations executed successfully
| 68 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 69 |  | All thyristor check-back signals are available.
| 70 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 71 |  | Measuring quantities are available and the values are within the specified range and phase.
| 72 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 73 |  | No Stuck Condition
| 74 |  | No False Tripping by DC Protection System
| 75 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 76 |  | No Tripping in AC side of converter Station

## Disturbance
Bipole Low Power DisturbanceTests
8-Disturbances Joint Power Control, Bi-Pole Ground Return
Test Objective | The test is to check the DC system performance during the disturbance.
Condition | Sr. No. | Station | Action | Equipment/ Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side at Matiari C/S | Both Poles will operate in Bipole Ground Return Mode see Status Table "BP-GR" |  |  | BI-Pole Mode of Operation
| 4 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 5 |  | All the Prerequisites as mentioned in DC Dispatch Plan should be met.
| 6 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 7 |  | All electrical connections are available.
| 8 |  | Protection settings and protective circuits trip sequences tests must be completed.
| 9 |  | AC-switchyard and associated protections and sequences, including breaker failure protection, must be active.
| 10 |  | Correct grounding of all equipment is available.
| 11 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 12 |  | Thyristor valves and valve hall is cleaned.
| 13 |  | Converter transformers are demagnetized.
| 14 |  | Air humidity and temperature in valve hall are within expected limits.
| 15 |  | Operation with Station Ground (Annex-D-VII must be successful)
| 16 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (600 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 17 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 18 |  | Return | Ground |  | Ground Return Mode
| 19 |  | Udc Mode | Normal |  | ±660 kV
| 20 |  | Telecom Mode | Operational
| 21 |  | Master Station | Matiari
| 22 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 23 |  |  | B | Standby
| 24 |  | Pole Control Protection (PCP) | A | ACTIVE
| 25 |  |  | B | Standby
| 26 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 27 |  | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 28 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 29 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Pole Trip, Open Line Fault at Electrode at Lahore (Sr. No. 16) (A4 6.3.1) | 30 | Matiari / Lahore | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 31 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 32 | Matiari & Lahore | Start the Pole-1, | Power | 400 MW
| 33 |  |  | Ramp Rate: | 50 MW/Min
| 34 |  | Wait to achieve Target Value | Max Time | 5 min
| 35 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 36 |  |  | DC Voltages | ±660kV
| 37 |  |  | RPC Operation | BP-11/13 , HP24/36
| 38 | Lahore |  | Extinction Angle (g) | 17°
| 39 |  |  | DC Voltages | Range to be mentioned
| 40 |  |  | RPC Operation | 2xHP12/24
| 41 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 42 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 43 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 44 | Lahore |  | 2xHP12/24
| 45 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 46 | Lahore | Instruct Test Director to simulate Electrode Line Open Circuit Protection Stage 2 Action, and then the NBGS would be automatically closed.
| 47 |  | Verify NBGS closed
| 48 |  | Instruct to Open WN3Q11 (Manually) | WN3Q11 | OPEN
| 49 | Matiari | Simulate Pole Bus Differential Protection Stage 2TRIP
| 50 | Matiari/Lahore | Verify | Pole-I Tripped
| 51 |  |  | Pole-2 consecutively trip because of overcurrent on the NBGS at Lahore
| 52 | Lahore | Instruct to Close WN3Q11 (Manually)
| 53 |  | Instruct to open NBGS
Pole Trip, Open Line Fault at Electrode at Matiari (Sr. No. 17) (A4 6.3.1) | 54 | Matiari | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 55 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 56 | Matiari & Lahore | Start the Pole-1, | Power | 400 MW
| 57 |  |  | Ramp Rate: | 50 MW/Min
| 58 |  | Wait to achieve Target Value | Max Time | 5 min
| 59 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 60 |  |  | DC Voltages | ±660kV
| 61 |  |  | RPC Operation | BP-11/13 , HP24/36
| 62 | Lahore |  | Extinction Angle (g) | 17°
| 63 |  |  | DC Voltages | Range to be mentioned
| 64 |  |  | RPC Operation | 2xHP12/24
| 65 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 66 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 67 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 68 | Lahore |  | 2xHP12/24
| 69 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 70 | Matiari | Instruct Test Director to simulate Electrode Line Open Circuit Protection Stage 2 Action, and then the NBGS would be automatically closed.
| 71 |  | Verify | NBGS is closed
| 72 |  | Instruct to Open WN3Q1
| 73 | Matiari | Simulate Pole Bus Differential Protection Stage 2TRIP Pole 2
| 74 | Matiari/Lahore | Verify | Pole 2 Tripped
| 75 |  |  | Pole 1 consecutively trip because of overcurrent on the NBGS at Matiari
Pole-1 in Operation while Pole-2 Undergoing Open Line Test (Sr. No. 18) (A4 6.3.2) | 76 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 77 | Matiari & Lahore | Start the Bi-pole | Power | 400 MW
| 78 |  |  | Ramp Rate: | 50 MW/Min
| 79 |  | Wait to achieve Target Value | Max Time | 5 min
| 80 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 81 |  |  | DC Voltages | ±660kV
| 82 |  |  | RPC Operation | BP-11/13 , HP24/36
| 83 | Lahore |  | Extinction Angle (g) | 17°
| 84 |  |  | DC Voltages | Range to be mentioned
| 85 |  |  | RPC Operation | 2xHP12/24
| 86 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 87 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 88 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 89 | Lahore |  | 2xHP12/24
| 90 | Matiari | Verify pole 1 and pole 2 in Bipolar Power Control Mode respectively.
| 91 | Matiari/Lahore | Stop pole 2
| 92 |  | Verify | Retard, Reduced Current |  | Block without BPP
| 93 | Lahore |  | Alpha angle | 90 | Block with BPP
| 94 | Matiari/Lahore |  | pole 1 rapidly boosts power for compensation
| 95 |  |  | Verify there is no influence on the transmitted bipolar power.
| 96 | Matiari/Lahore | initiate the sequence of Closing Valve Hall Ground Switches, and the converters in both stations are in GROUNDED condition.
| 97 | Matiari/Lahore | Verify | Steady operation in pole 1
| 98 |  |  | No transient change in bipole power
| 99 |  |  | Sequential control fulfilled
| 100 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions of Pole-2
| 101 | Lahore | Instruct to Open WP2Q11
| 102 |  | Verify WP2Q11 open
| 103 | Matiari | Verify WP2Q11 closed
| 104 | Matiari | set Pole 2 in separate control and OLT automatic control mode.
| 105 | Matiari | Initiate the automatic open line test with line on pole 2.
| 106 | Matiari/Lahore | Verify | Steady operation in pole 1
| 107 |  |  | No transient change in bipole power
| 108 |  |  | Sequential control fulfilled
| 109 |  |  | Open line test completes successfully on Pole 2
| 110 | Lahore | Instruct to close WP2Q11
| 111 |  | Verify WP2Q11 closed
| 112 | Matiari | Instruct to open WP2Q11
| 113 |  | Verify WP2Q11 open
| 114 | Lahore | Initiate the automatic open line test with line on pole 2.
| 115 | Matiari/Lahore | Verify | Steady operation in pole 1
| 116 |  |  | No transient change in bipole power
| 117 |  |  | Sequential control fulfilled
| 118 |  |  | Open line test completes successfully on Pole 2
| 119 | Matiari/Lahore | Stop Pole 1
Pole-2 in Operation while Pole-1 Undergoing Open Line Test (Sr. No. 19) (A4 6.3.2) | 120 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 121 | Matiari & Lahore | Start the Bi-pole | Power | 400 MW
| 122 |  |  | Ramp Rate: | 50 MW/Min
| 123 |  | Wait to achieve Target Value | Max Time | 5 min
| 124 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 125 |  |  | DC Voltages | ±660kV
| 126 |  |  | RPC Operation | BP-11/13 , HP24/36
| 127 | Lahore |  | Extinction Angle (g) | 17°
| 128 |  |  | DC Voltages | Range to be mentioned
| 129 |  |  | RPC Operation | 2xHP12/24
| 130 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 131 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 132 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 133 | Lahore |  | 2xHP12/24
| 134 | Matiari/Lahore | Verify pole 1 and pole 2 in Bipolar Power Control Mode respectively.
| 135 | Matiari/Lahore | Stop pole 1
| 136 | Matiari | Verify | Retard, Reduced Current |  | Block without BPP
| 137 | Lahore |  | Alpha angle | 90 | Block with BPP
| 138 | Matiari/Lahore |  | pole 2 rapidly boosts power for compensation
| 139 |  |  | Verify there is no influence on the transmitted bipolar power.
| 140 | Matiari/Lahore | initiate the sequence of Closing Valve Hall Ground Switches, and the converters in both stations are in GROUNDED condition.
| 141 |  | Verify | Steady operation in pole 2
| 142 |  |  | No transient change in bipole power
| 143 |  |  | Sequential control fulfilled
| 144 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions of Pole-1
| 145 | Lahore | Instruct to Open WP1Q11
| 146 |  | Verify WP1Q11 open
| 147 | Matiari | set Pole 1 in separate control and OLT automatic control mode.
| 148 | Matiari | Initiate the automatic open line test with line on pole 1.
| 149 | Matiari/lahore | Verify | Steady operation in pole 1
| 150 |  |  | No transient change in bipole power
| 151 |  |  | Sequential control fulfilled
| 152 |  |  | Open line test completes successfully on Pole 1
| 153 | Lahore | Instruct to close WP1Q11
| 154 |  | Verify WP2Q11 WP1Q11 closed
| 155 | Matiari | Instruct to open WP1Q11
| 156 |  | Verify WP2Q11 open
| 157 | Lahore | Initiate the automatic open line test with line on pole 1.
| 158 | Matiari/lahore | Verify | Steady operation in pole 1
| 159 |  |  | No transient change in bipole power
| 160 |  |  | Sequential control fulfilled
| 161 |  |  | Open line test completes successfully on Pole 1
| 162 | Matiari/Lahore | Stop Pole 2
Bipole Operation, Simulate Electrode Line Unbalance Fault (Sr. No. 20) (A4 6.3.3) | 163 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 164 | Matiari & Lahore | Start the Bi-pole | Power | 400 MW
| 165 |  |  | Ramp Rate: | 50 MW/Min
| 166 |  | Wait to achieve Target Value | Max Time | 5 min
| 167 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 168 |  |  | DC Voltages | ±660kV
| 169 |  |  | RPC Operation | BP-11/13 , HP24/36
| 170 | Lahore |  | Extinction Angle (g) | 17°
| 171 |  |  | DC Voltages | Range to be mentioned
| 172 |  |  | RPC Operation | 2xHP12/24
| 173 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 174 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 175 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 176 | Lahore |  | 2xHP12/24
| 177 | Matiari | Verify pole 1 and pole 2 in Bipolar Power Control Mode respectively.
| 178 |  | Order pole 2 in Pole Power Control Mode.
| 179 |  | Ramp Up power of Pole-2 | 200 MW | 400 MW | 50 MW/min
| 180 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 600 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 181 | Lahore | Instruct Test Commander to simulate the Electrode Line Unbalance Fault
| 182 | Matiari/Lahore | Verify | Electrode line unbalance protection acts correctly
| 183 |  |  | Electrode line current < 30A
| 184 |  |  | The power of pole 2 would decrease to 200MW for balancing the electrode line current.
Simulation of IDNC CT Transmitter Power Source Fault (Sr. No. 21) (A4 6.3.4) | 185 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 186 | Matiari & Lahore | Start the Bi-pole | Power | 400 MW
| 187 |  |  | Ramp Rate: | 50 MW/Min
| 188 |  | Wait to achieve Target Value | Max Time | 5 min
| 189 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 190 |  |  | DC Voltages | ±660kV
| 191 |  |  | RPC Operation | BP-11/13 , HP24/36
| 192 | Lahore |  | Extinction Angle (g) | 17°
| 193 |  |  | DC Voltages | Range to be mentioned
| 194 |  |  | RPC Operation | 2xHP12/24
| 195 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 196 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 197 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 198 | Lahore |  | 2xHP12/24
| 199 | Matiari | Verify pole 1 and pole 2 in Bipolar Power Control Mode respectively.
| 200 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 201 | Matiati | Instruct Test Commander to Simulate fault of PI IDNC CT transmitter power source in active system (e.g. PCPA) at Matiari/Terminal LAHORE station separately by turn off the corresponding power source
| 202 | Matiari/Lahore | Verify | continuing steady operation of the transmission
| 203 |  |  | active system is switched.
| 204 |  |  | No transient or unexpected time delay
AC Auxiliary Power 400 V Switchover (Sr. No. 22) (A4 6.3.5) | 205 | Matiari | Verify pole 1 and pole 2 in Bipolar Power Control Mode respectively.
| 206 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 207 | Matiari & Lahore | Start the Bi-pole | Power | 400 MW
| 208 |  |  | Ramp Rate: | 50 MW/Min
| 209 |  | Wait to achieve Target Value | Max Time | 5 min
| 210 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 211 |  |  | DC Voltages | ±660kV
| 212 |  |  | RPC Operation | BP-11/13 , HP24/36
| 213 | Lahore |  | Extinction Angle (g) | 17°
| 214 |  |  | DC Voltages | Range to be mentioned
| 215 |  |  | RPC Operation | 2xHP12/24
| 216 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 217 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 218 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 219 | Lahore |  | 2xHP12/24
| 220 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 221 | Matiari | Instruct to Manually Open Switch | 111 | Open
| 222 |  | Verify automatic action of following switches | 411 | OFF
| 223 |  |  | 410 | ON
| 224 |  | Instruct to Manually CLOSE Switch | 111 | CLOSE
| 225 |  | Verify automatic action of following switches | 411 | ON
| 226 |  |  | 410 | OFF
| 227 |  | Instruct to Manually OPEN Switch | 112 | Open
| 228 |  | Verify automatic action of following switches | 412 | OFF
| 229 |  |  | 410 | ON
| 230 |  | Instruct to Manually CLOSE Switch | 112 | CLOSE
| 231 |  | Verify automatic action of following switches | 412 | ON
| 232 |  |  | 410 | OFF
| 233 |  | Instruct to Manually OPEN Switch | 121 | OPEN
| 234 |  | Verify automatic action of following switches | 421 | OFF
| 235 |  |  | 420 | ON
| 236 |  | Instruct to Manually CLOSE Switch | 121 | OPEN
| 237 |  | Verify automatic action of following switches | 421 | ON
| 238 |  |  | 420 | OFF
| 239 |  | Instruct to Manually OPEN Switch | 122 | OPEN
| 240 |  | Verify automatic action of following switches | 422 | OFF
| 241 |  |  | 420 | ON
| 242 |  | Instruct to Manually CLOSE Switch | 122 | CLOSE
| 243 |  | Verify automatic action of following switches | 422 | ON
| 244 |  |  | 420 | OFF
| 245 | Lahore | Instruct to Manually Open Switch | 111 | Open
| 246 |  | Verify automatic action of following switches | 411 | OFF
| 247 |  |  | 410 | ON
| 248 |  | Instruct to Manually CLOSE Switch | 111 | CLOSE
| 249 |  | Verify automatic action of following switches | 411 | ON
| 250 |  |  | 410 | OFF
| 251 |  | Instruct to Manually OPEN Switch | 112 | Open
| 252 |  | Verify automatic action of following switches | 412 | OFF
| 253 |  |  | 410 | ON
| 254 |  | Instruct to Manually CLOSE Switch | 112 | CLOSE
| 255 |  | Verify automatic action of following switches | 412 | ON
| 256 |  |  | 410 | OFF
| 257 |  | Instruct to Manually OPEN Switch | 121 | OPEN
| 258 |  | Verify automatic action of following switches | 421 | OFF
| 259 |  |  | 420 | ON
| 260 |  | Instruct to Manually CLOSE Switch | 121 | OPEN
| 261 |  | Verify automatic action of following switches | 421 | ON
| 262 |  |  | 420 | OFF
| 263 |  | Instruct to Manually OPEN Switch | 122 | OPEN
| 264 |  | Verify automatic action of following switches | 422 | OFF
| 265 |  |  | 420 | ON
| 266 |  | Instruct to Manually CLOSE Switch | 122 | CLOSE
| 267 |  | Verify automatic action of following switches | 422 | ON
| 268 |  |  | 420 | OFF
Test Acceptance Criteria | 269 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 270 |  | All Operations executed successfully
| 271 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 272 |  | All thyristor check-back signals are available.
| 273 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 274 |  | Measuring quantities are available and the values are within the specified range and phase.
| 275 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 276 |  | No Stuck Condition
| 277 |  | No False Tripping by DC Protection System
| 278 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 279 |  | No Tripping in AC side of converter Station

## FCT
Bipole Low Power DisturbanceTests
9-Frequency Control Test Joint Power Control, Bi-Pole Ground Return
Test Objective | The test is to check the basic function of frequency control of DC system
Condition | Sr. No. | Station | Action | Equipment/ Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side at Matiari C/S | Both Poles will operate in Bipole Ground Return Mode see Status Table "BP-GR" |  |  | BI-Pole Mode of Operation
| 4 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 5 |  | All the Prerequisites as mentioned in DC Dispatch Plan should be met.
| 6 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 7 |  | All electrical connections are available.
| 8 |  | Protection settings and protective circuits trip sequences tests must be completed.
| 9 |  | AC-switchyard and associated protections and sequences, including breaker failure protection, must be active.
| 10 |  | Correct grounding of all equipment is available.
| 11 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 12 |  | Thyristor valves and valve hall is cleaned.
| 13 |  | Converter transformers are demagnetized.
| 14 |  | Air humidity and temperature in valve hall are within expected limits.
| 15 |  | Disturbances (Annex-D-VIII must be successful)
| 16 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (500 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 17 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 18 |  | Return | Ground |  | Ground Return Mode
| 19 |  | Udc Mode | Normal |  | ±660 kV
| 20 |  | Telecom Mode | Operational
| 21 |  | Master Station | Matiari
| 22 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 23 |  |  | B | Standby
| 24 |  | Pole Control Protection (PCP) | A | ACTIVE
| 25 |  |  | B | Standby
| 26 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 27 |  | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 28 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 29 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Frequency Control Test | 30 | Matiari/Lahore | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 31 | Matiari | Verify Matiari is Master Station.
| 32 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 33 | Matiari & Lahore | Start the BiPole | Power | 400 MW
| 34 |  |  | Ramp Rate: | 50 MW/Min
| 35 |  | Wait to achieve Target Value | Max Time | 5 min
| 36 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 37 |  |  | DC Voltages | ±660 kV
| 38 |  |  | Electrode Current | <30 Amps
| 39 |  |  | RPC Operation | BP-11/13 , HP24/36
| 40 | Lahore |  | Extinction Angle (g) | 17°
| 41 |  |  | DC Voltages | Range to be mentioned
| 42 |  |  | RPC Operation | 2xHP12/24
| 43 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 44 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 45 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 46 | Lahore |  | 2xHP12/24
Frequency Control Test in Matiari Converter Station (Sr. No. 23) (A4 8.3.1) | 47 | Matiari | Verify | The DC power corresponding to 1Hz of frequency change is 1000MW
| 48 |  |  | The frequency deviation deadband is ±0.1Hz.
| 49 |  |  | Upper and lower output limits of frequency control is ±200MW.
| 50 |  | NPCC makes sure, parallel AC corridor has margin for sharing 200 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 51 |  | Simulate the frequency of the AC power grid connected the Matiari station to 49.8Hz, with a difference of 0.1Hz (0.1Hz has been subtracted from the deadband), and the duration is 5000ms.
| 52 |  | Verify | The DC power ramps down about 100MW.
| 53 |  |  | After the frequency deviation disappears, the DC transmission power will automatically return to the value before the test.
| 54 |  | Simulate the frequency of the AC power grid connected the Matiari station to 50.2Hz, with a difference of 0.1Hz (0.1Hz has been subtracted from the deadband), and the duration is 5000ms.
| 55 |  | Verify | The DC power ramps up about 100MW.
| 56 |  |  | After the frequency deviation disappears, the DC transmission power will automatically return to the value before the test.
Frequency Control Test in Lahore Converter Station (Sr. No. 24) (A4 8.3.2) | 57 | Lahore | Initiate Master Sequence at Lahore Station
| 58 |  | Verify | The DC power corresponding to 1Hz of frequency change is 1000MW
| 59 |  |  | The frequency deviation deadband is ±0.1Hz.
| 60 |  |  | Upper and lower output limits of frequency control is ±200MW.
| 61 |  | NPCC makes sure, parallel AC corridor has margin for sharing 200 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 62 |  | Simulate the frequency of the AC power grid connected the Matiari station to 49.8Hz, with a difference of 0.1Hz (0.1Hz has been subtracted from the deadband), and the duration is 5000ms.
| 63 |  | Verify | The DC power ramps up about 100MW.
| 64 |  |  | After the frequency deviation disappears, the DC transmission power will automatically return to the value before the test.
| 65 |  | Simulate the frequency of the AC power grid connected the Matiari station to 50.2Hz, with a difference of 0.1Hz (0.1Hz has been subtracted from the deadband), and the duration is 5000ms.
| 66 |  | Verify | The DC power ramps down about 100MW.
| 67 |  |  | After the frequency deviation disappears, the DC transmission power will automatically return to the value before the test.
Test Acceptance Criteria | 68 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 69 |  | All Operations executed successfully
| 70 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 71 |  | All thyristor check-back signals are available.
| 72 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 73 |  | Measuring quantities are available and the values are within the specified range and phase.
| 74 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 75 |  | No Stuck Condition
| 76 |  | No False Tripping by DC Protection System
| 77 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 78 |  | No Tripping in AC side of converter Station

## IOT GR Rev
Bipole Low Power Tests
10-Initial Operation Tests, Bi-Pole Ground Return Operation, Reversed Power Direction Joint Power Control
Test Objective | The test is to check the basic function of DC system during reversed power direction.
Condition | Sr. No. | Station | Action | Equipment/ Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side at Matiari C/S | Both Poles will operate in Bipole Ground Return Mode see Status Table "BP-GR" |  |  | BI-Pole Mode of Operation
| 4 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 5 |  | All the Prerequisites as mentioned in DC Dispatch Plan should be met.
| 6 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 7 |  | All electrical connections are available.
| 8 |  | Protection settings and protective circuits trip sequences tests must be completed.
| 9 |  | AC-switchyard and associated protections and sequences, including breaker failure protection, must be active.
| 10 |  | Correct grounding of all equipment is available.
| 11 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 12 |  | Thyristor valves and valve hall is cleaned.
| 13 |  | Converter transformers are demagnetized.
| 14 |  | Air humidity and temperature in valve hall are within expected limits.
| 15 |  | Frequency Control Test (Annex-D-IX must be successful)
| 16 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (400 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 17 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Reverse |  | Lahore to Matiari
| 18 |  | Return | Ground |  | Ground Return Mode
| 19 |  | Udc Mode | Normal |  | ±660kV
| 20 |  | Telecom Mode | Operational
| 21 |  | Master Station | Matiari
| 22 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 23 |  |  | B | Standby
| 24 |  | Pole Control Protection (PCP) | A | ACTIVE
| 25 |  |  | B | Standby
| 26 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 27 |  | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 28 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 29 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
BiPole Start/Stop (Sr. No. 25) (A4 10.3.1) | 30 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 31 |  | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 32 | Lahore | Start the BIPOLE | Power | 400 MW
| 33 |  |  | Ramp Rate: | 50 MW/Min
| 34 |  | Wait to achieve Target Value | Max Time | 5 min
| 35 | Lahore | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 36 |  |  | DC Voltages | ±660 kV
| 37 |  |  | RPC Operation | 2xHP12/24
| 38 | Matiari |  | Extinction Angle (g) | 17°
| 39 |  |  | DC Voltages | Range to be mentioned
| 40 |  |  | RPC Operation | BP-11/13 , HP24/36
| 41 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 42 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 43 | Lahore | Verify RPC action | 2xHP12/24
| 44 | Matiari |  | BP-11/13, HP-24/36
| 45 | Matiari/Lahore | Stop the Bipole
| 46 | Lahore | Verify Performance parameters | Y-Block
| 47 |  |  | Retard, Reduced Current |  | Block without BPP
| 48 | Matiari |  | Y-Block
| 49 |  |  | Alpha angle | 90 | Block with BPP
Control System Switchover (Sr. No. 26) (A4 10.3.2) | 50 | Lahore | Verify Ready for Operation Conditions.
| 51 |  | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 52 |  | Start the Pole-1 | Power | 400 MW
| 53 |  |  | Ramp Rate: | 50 MW/Min
| 54 | Matiari | Verify | PCP-A | ACTIVE
| 55 |  | Switch Control System | PCP-A to | PCP-B
| 56 |  | Verify | Continuous Steady Operation of the transmission
| 57 |  |  | PCP-B is active
| 58 |  |  | No Transients or unexpected delays
| 59 |  | Switch Control System | PCP-B to | PCP-A
| 60 |  | Verify | Continuous Steady Operation of the transmission
| 61 |  |  | PCP-A is active
| 62 |  |  | No Transients or unexpected delays
| 63 |  | Verify | SC-A | ACTIVE
| 64 |  | Switch Control System | SC-A to | SC-B
| 65 |  | Verify | Continuous Steady Operation of the transmission
| 66 |  |  | SC-B is active
| 67 |  |  | No Transients or unexpected delays
| 68 |  | Switch Control System | SC-B to | SC-A
| 69 |  | Verify | Continuous Steady Operation of the transmission
| 70 |  |  | SC-A is active
| 71 |  |  | No Transients or unexpected delays
| 72 | Lahore | Verify | PCP-A | ACTIVE
| 73 |  | Switch Control System | PCP-A to | PCP-B
| 74 |  | Verify | Continuous Steady Operation of the transmission
| 75 |  |  | PCP-B is active
| 76 |  |  | No Transients or unexpected delays
| 77 |  | Switch Control System | PCP-B to | PCP-A
| 78 |  | Verify | Continuous Steady Operation of the transmission
| 79 |  |  | PCP-A is active
| 80 |  |  | No Transients or unexpected delays
| 81 |  | Verify | SC-A | ACTIVE
| 82 |  | Switch Control System | SC-A to | SC-B
| 83 |  | Verify | Continuous Steady Operation of the transmission
| 84 |  |  | SC-B is active
| 85 |  |  | No Transients or unexpected delays
| 86 |  | Switch Control System | SC-B to | SC-A
| 87 |  | Verify | Continuous Steady Operation of the transmission
| 88 |  |  | SC-A is active
| 89 |  |  | No Transients or unexpected delays
| 90 | Matiari/Lahore | Stop the Bipole
| 91 | Lahore | Verify Performance parameters | Retard, Reduced Current
| 92 | Matiari |  | Alpha angle | 90°
Test Acceptance Criteria | 93 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 94 |  | All Operations executed successfully
| 95 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 96 |  | All thyristor check-back signals are available.
| 97 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 98 |  | Measuring quantities are available and the values are within the specified range and phase.
| 99 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 100 |  | No Stuck Condition
| 101 |  | No False Tripping by DC Protection System
| 102 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 103 |  | No Tripping in AC side of converter Station

## PXYZ (R)
Bipole Low Power Tests
11-Protective Trip X, Y, and Z, Reversed Power Direction Joint Power Control, Normal Power Direction, Bi-Pole Ground Return
Test Objective | The test objective is to check the protection trip function.
Condition | Sr. No. | Station | Action | Equipment/ Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side at Matiari C/S | Both Poles will operate in Bipole Ground Return Mode see Status Table "BP-GR" |  |  | BI-Pole Mode of Operation
| 4 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 5 |  | All the Prerequisites as mentioned in DC Dispatch Plan should be met.
| 6 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 7 |  | All electrical connections are available.
| 8 |  | Protection settings and protective circuits trip sequences tests must be completed.
| 9 |  | AC-switchyard and associated protections and sequences, including breaker failure protection, must be active.
| 10 |  | Correct grounding of all equipment is available.
| 11 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 12 |  | Thyristor valves and valve hall is cleaned.
| 13 |  | Converter transformers are demagnetized.
| 14 |  | Air humidity and temperature in valve hall are within expected limits.
| 15 |  | Initial Operation Tests, Reversed Power Direction (Annex-D-X must be successful)
| 16 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (400 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 17 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Reversed |  | Lahore to Matiari
| 18 |  | Return | Ground |  | Ground Return Mode
| 19 |  | Udc Mode | Normal |  | ±660kV
| 20 |  | Telecom Mode | Operational
| 21 |  | Master Station | Matiari
| 22 | Configuration Setting at Matiari & Lahore C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 23 |  |  | B | Standby
| 24 |  | Pole Control Protection (PCP) | A | ACTIVE
| 25 |  |  | B | Standby
| 26 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 27 |  | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 28 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 29 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Protective Trip X in Rectifier with Telecommunication (Sr. No. 27) (A4 11.3.1) | 30 | Lahore | Verify Ready for Operation Conditions.
| 31 |  | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 32 |  | Start the Pole-1 | Power | 400 MW
| 33 |  |  | Ramp Rate: | 50 MW/min
| 34 |  | Wait to achieve Target Value | Max Time | 5 min
| 35 |  | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 36 |  |  | DC Voltages | ±660 kV
| 37 |  |  | RPC Operation | 2xHP12/24
| 38 | Matiari |  | Extinction Angle (g) | 17°
| 39 |  |  | DC Voltages | Range to be mentioned
| 40 |  |  | RPC Operation | BP-11/13 , HP24/36
| 41 | Matiari/Lahore | Verify stable operation at minimum power.
| 42 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 43 | Lahore | Verify RPC action | 2xHP12/24
| 44 | Matiari |  | BP-11/13 , HP24/36
| 45 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 46 | Lahore | Simulate Valve short Circuit Protection Stage 2 TRIP in Pole 1
| 47 |  | Verify Protection Functions | X-block
| 48 |  |  | Trip Action | Converter T/F AC Breakers
| 49 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 50 |  |  | Start Breaker Failure Protection
| 51 |  |  | Pole IsolationSequence
| 52 | Matiari |  | Normal Y-block sequence
| 53 | Matiari/Lahore | Verify there is no influence on the transmitted bipolar power.
| 54 | Matiari | Stop Pole 2
| 55 |  | Verify Performance parameters | Retard, Reduced Current |  | Block without BPP
| 56 | Lahore |  | Alpha angle | 90 | Block with BPP
Protective Trip Y in inverter with TELECOM (Sr. No. 28) (A4 11.3.2) | 57 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 58 | Matiari | Start the Bipole | Power | 400 MW
| 59 |  |  | Ramp Rate: | 50 MW/min
| 60 |  | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 61 |  | Simulate Station Ground Overcurrent Protection Action in Pole 1
| 62 | Lahore | Verify Protection Functions | Y-block
| 63 |  |  | Retard and start by-pass pair
| 64 |  |  | Trip Action | Converter T/F AC Breakers
| 65 |  |  | Pole IsolationSequence
| 66 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 67 |  |  | Start Breaker Failure Protection
| 68 | Matiari |  | Pole Isolation
| 69 | Matiari/Lahore C/S DC side | Verify there is no influence on the transmitted bipolar power.
| 70 | Matiari | Stop Pole 2
Protective Trip Z in rectifier with TELECOM (Sr. No. 29) (A4 11.3.3) | 71 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 72 | Lahore | Start the Bipole | Power | 400 MW
| 73 |  |  | Ramp Rate: | 50 MW/min
| 74 |  | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 75 |  | Simulate Pole Bus Differential Protection Stage-2 Trip in Pole 2
| 76 |  | Verify Protection Functions | Z-block
| 77 |  |  | Trip Action | Converter T/F AC Breakers
| 78 |  |  | Pole IsolationSequence
| 79 |  |  | Start Breaker Failure Protection
| 80 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 81 | Matiari |  | Normal Y-block sequence
| 82 | Matiari | Stop Pole 1
Test Acceptance Criteria | 83 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 84 |  | All Operations executed successfully
| 85 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 86 |  | All thyristor check-back signals are available.
| 87 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 88 |  | Measuring quantities are available and the values are within the specified range and phase.
| 89 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 90 |  | No Stuck Condition
| 91 |  | No False Tripping by DC Protection System
| 92 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 93 |  | No Tripping in AC side of converter Station

## PC (R)
Bipole Low Power Tests
12- Pole Compensation and disturbance test, Reversed Power Direction Joint Power Control, Bi-Pole Ground Return
Test Objective | The test objective is to check the pole compensation during reversed power direction.
Condition | Sr. No. | Station | Action | Equipment/ Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side at Matiari C/S | Both Poles will operate in Bipole Ground Return Mode see Status Table "BP-GR" |  |  | BI-Pole Mode of Operation
| 4 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 5 |  | All the Prerequisites as mentioned in DC Dispatch Plan should be met.
| 6 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 7 |  | All electrical connections are available.
| 8 |  | Protection settings and protective circuits trip sequences tests must be completed.
| 9 |  | AC-switchyard and associated protections and sequences, including breaker failure protection, must be active.
| 10 |  | Correct grounding of all equipment is available.
| 11 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 12 |  | Thyristor valves and valve hall is cleaned.
| 13 |  | Converter transformers are demagnetized.
| 14 |  | Set tap changer to position giving lowest valve voltage
| 15 |  | Protective Trip X, Y, and Z, Reversed Power Direction (Annex-D-XI must be successful)
| 16 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (800 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 17 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Reversed |  | Matiari to Lahore
| 18 |  | Return | Ground |  | Ground Return Mode
| 19 |  | Udc Mode | Normal |  | ±660kV
| 20 |  | Telecom Mode | Operational
| 21 |  | Master Station | Matiari
| 22 | Configuration Setting at Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 23 |  |  | B | Standby
| 24 |  | Pole Control (PCP) | A | ACTIVE
| 25 |  |  | B | Standby
| 26 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 27 |  | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 28 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 29 |  | Reactive Power Control Variable | U-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Pre-Test Conditions & Configurations (AC/DC) | 30 | Configuration Setting at Lahore C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 31 |  |  | B | Standby
| 32 |  | Pole Control (PCP) | A | ACTIVE
| 33 |  |  | B | Standby
| 34 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 35 | Configuration Setting at Lahore C/S DC side | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 36 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 37 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Bipolar Power Ramping (Sr. No. 30) (A4 12.3.1) | 38 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 39 |  | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 40 | Lahore | Start the BiPole | Power | 400 MW
| 41 |  |  | Ramp Rate: | 50MW/Min
| 42 |  | Wait to achieve Target Value | Max Time | 5 min
| 43 |  | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 44 |  |  | DC Voltages | ±660 kV
| 45 |  |  | RPC Operation | 2xHP12/24
| 46 | Matiari |  | Extinction Angle (g) | 17°
| 47 |  |  | DC Voltages | Range to be mentioned
| 48 |  |  | RPC Operation | BP-11/13 , HP24/36
| 49 | Matiari/Lahore | Verify stable operation at minimum power
| 50 | Lahore | Verify RPC action | 2xHP12/24
| 51 | Matiari |  | BP-11/13 , HP24/36
| 52 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 53 | Matiari | Activate the emergency stop push-button in pole 2 in Matiari Station.
| 54 | Matiari/Lahore | Verify | there is no influence on the transmitted bipolar power.
| 55 | Matiari | Initiate Pole Power Control for Pole 2
| 56 | Matiari | Start the Pole-2 | Power | 200 MW
| 57 |  |  | Ramp Rate: | 50MW/Min
| 58 | Lahore | Wait to achieve Target Value | Max Time | 5 min
| 59 |  | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 60 |  |  | DC Voltages | ±660 kV
| 61 |  |  | RPC Operation | 2xHP12/24
| 62 | Matiari |  | Extinction Angle (g) | 17°
| 63 |  |  | DC Voltages | Range to be mentioned
| 64 |  |  | RPC Operation | BP-11/13 , HP24/36
| 65 | Matiari/Lahore | Verify stable operation at minimum power
| 66 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 67 | Lahore |  | HP-12/24, HP-12/24
| 68 | Matiari | Order pole 2 in Bipolar Power Control Model.
| 69 | Matiari/Lahore | Verify | there is no influence on the transmitted bipolar power.
| 70 | Matiari | Ramp Up | 400 MW | 800 MW | 50 MW
| 71 | Lahore | Verify (During Ramping) | PCP-A | ACTIVE
| 72 |  | Manual Switch Control System (During Ramping) | PCP-A to | PCP-B
| 73 |  | Manual Switch Control System | PCP-B to | PCP-A
| 74 |  | Verify (During Ramping) | SC-A | ACTIVE
| 75 |  | Manual Switch Control System (During Ramping) | SC-A to | SC-B
| 76 |  | Manual Switch Control System | SC-B to | SC-A
Bipolar Power Ramping (Sr. No. 30) (A4 12.3.1) | 77 | Matiari | Verify (During Ramping) | PCP-A | ACTIVE
| 78 |  | Manual Switch Control System (During Ramping) | PCP-A to | PCP-B
| 79 |  | Manual Switch Control System | PCP-B to | PCP-A
| 80 |  | Verify (During Ramping) | SC-A | ACTIVE
| 81 |  | Manual Switch Control System (During Ramping) | SC-A to | SC-B
| 82 |  | Manual Switch Control System | SC-B to | SC-A
| 83 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 84 |  |  | PCP-A & SC-A is active
| 85 |  |  | power reaches the reference value after ramping is completed
| 86 |  |  | No Transients or unexpected time delays
| 87 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 200 MW with DC System. (Sudden load sharing from AC corridor to DC corridor will happen in next step)
| 88 | Matiari | Ramp Down | 800 MW | 400 MW | 50 MW
| 89 | Lahore | Verify (During Ramping) | PCP-A | ACTIVE
| 90 |  | Manual Switch Control System (During Ramping) | PCP-A to | PCP-B
| 91 |  | Manual Switch Control System | PCP-B to | PCP-A
| 92 |  | Verify (During Ramping) | SC-A | ACTIVE
| 93 |  | Manual Switch Control System (During Ramping) | SC-A to | SC-B
| 94 |  | Manual Switch Control System | SC-B to | SC-A
| 95 | Matiari | Verify (During Ramping) | PCP-A | ACTIVE
| 96 |  | Manual Switch Control System (During Ramping) | PCP-A to | PCP-B
| 97 |  | Manual Switch Control System | PCP-B to | PCP-A
| 98 |  | Verify (During Ramping) | SC-A | ACTIVE
| 99 |  | Manual Switch Control System (During Ramping) | SC-A to | SC-B
| 100 |  | Manual Switch Control System | SC-B to | SC-A
| 101 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 102 |  |  | PCP-A is active
| 103 |  |  | power reaches the reference value after ramping is completed
| 104 |  |  | No Transients or unexpected time delays
| 105 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 200 MW with DC System. (Sudden load sharing from AC corridor to DC corridor will happen in next step)
| 106 | Matiari | Ramp Up | 400 MW | 800 MW | 999 MW
| 107 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 108 |  |  | power reaches the reference value after ramping is completed
| 109 |  |  | No Transients
Bipole Operation, Pole 2 Power Ramping with / without Telecom. Reverse Power Direction (Sr. No. 31) (A4 12.3.2) | 110 | Matiari /Lahore | Verify Pole-I and Pole-II is in stable Bi-Pole Power Control Mode at 800 MW in sequence to test above.
| 111 |  | Order Pole-2 in Pole Power Control Mode, (Pole-I is in Bi-Pole Mode)
| 112 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 113 |  |  | Pole Power Control Mode achieved successfully in Pole 2
| 114 |  |  | No Transients
| 115 | Lahore | Order Pole-2 in Pole Current Control Mode, (Pole-I is in Bi-Pole Power Mode)
| 116 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 117 |  |  | Pole Current Control Mode achieved successfully in Pole 2
| 118 |  |  | No Transients
| 119 | Matiari | Ramp Up | 606 Amps | 800 Amps | 50 Amps/Min
| 120 | Lahore | Verify (During Ramping) | PCP-A | ACTIVE
| 121 |  | Manual Switch Control System (During Ramping) | PCP-A to | PCP-B
| 122 |  |  | PCP-B to | PCP-A
| 123 | Matiari | Verify (During Ramping) | PCP-A | ACTIVE
| 124 |  | Manual Switch Control System (During Ramping) | PCP-A to | PCP-B
| 125 |  |  | PCP-B to | PCP-A
| 126 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 127 |  |  | PCP-A is active
| 128 |  |  | current reaches the reference value after ramping is completed
| 129 |  |  | No Transients
| 130 | Lahore | Ramp Down | 800 Amps | 606 Amps | 50 Amps/Min
| 131 |  | Disabled the telecommunication in both channels in Pole 2 during the ramping process
| 132 | Matiari /Lahore | Verify | Emergency Pole Current Control will be activated in Pole-2
| 133 |  |  | Pole 1 telecom remains on and Pole 1 is in Bipole Power Control.
| 134 |  |  | The ramping would be continuing with a reduced ramp rate and the current reference value would be reached when the telecommunication is disabled
| 135 |  |  | No Transients
| 136 | Matiari/Lahore | Verify Two poles are in stable operation at 800MW
| 137 | Matiari | Restore the telecommunication of Pole-2
Bipole Operation, Pole 1 Power Ramping with / without Telecom. Reverse Power Direction (Sr. No. 32) (A4 12.3.2) | 138 | Matiari | Order Pole 2 in Bipolar Power Control Model.
| 139 | Matiari /Lahore | Verify Pole-I and Pole-II is in stable Bi-Pole Power Control Mode at 800 MW
| 140 |  | Order Pole-1 in Pole Power Control Mode, (Pole-2 is in Bi-Pole Mode)
| 141 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 142 |  |  | Pole Power Control Mode achieved successfully in Pole 1
| 143 |  |  | No Transients
| 144 | Lahore | Order Pole-1 in Monopolar Current Control Mode, (Pole-2 is in Bi-Pole Power Mode)
| 145 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 146 |  |  | Pole Current Control Mode achieved successfully in Pole 1
| 147 |  |  | No Transients
| 148 | Matiari | Ramp Up | 606 Amps | 800 Amps | 50 Amps/Min
| 149 | Lahore | Verify (During Ramping) | PCP-A | ACTIVE
| 150 |  | Manual Switch Control System (During Ramping) | PCP-A to | PCP-B
| 151 |  |  | PCP-B to | PCP-A
| 152 | Matiari | Verify (During Ramping) | PCP-A | ACTIVE
| 153 |  | Manual Switch Control System (During Ramping) | PCP-A to | PCP-B
| 154 |  |  | PCP-B to | PCP-A
| 155 | Matiari /Lahore | Verify | Continuous Steady Operation of the transmission
| 156 |  |  | PCP-A is active
| 157 |  |  | current reaches the reference value after ramping is completed
| 158 |  |  | No Transients
| 159 | Lahore | Ramp Down | 800 Amps | 606 Amps | 50 Amps/Min
| 160 |  | Disabled the telecommunication in both channels in Pole 1 during the ramping process
| 161 | Matiari /Lahore | Verify | Emergency Pole Current Control will be activated in Pole-1
| 162 |  |  | Pole 2 telecom remains on and Pole 2 is in Bipole Power Control.
| 163 |  |  | The ramping would be continuing with a reduced ramp rate and the current reference value would be reached when the telecommunication is disabled.
| 164 |  |  | No Transients
| 165 | Matiari | Verify Two poles are in stable operation at 800MW
| 166 | Matiari | Restore the telecommunication of Pole-1
Simulated Pole1 DC Line Fault (only Lahore) (Sr. No. 33) (A4 12.3.3) | 167 | Matiari | Order Pole 1 in Bipolar Power Control Model.
| 168 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 169 |  | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 170 | Lahore | Start the BIPOLE | Power | 400 MW
| 171 |  |  | Ramp Rate: | 50 MW/Min
| 172 |  | Wait to achieve Target Value | Max Time | 5 min
| 173 | Lahore | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 174 |  |  | DC Voltages | ±660kV
| 175 |  |  | RPC Operation | 2xHP12/24
| 176 | Matiari |  | Extinction Angle (g) | 17°
| 177 |  |  | DC Voltages | Range to be mentioned
| 178 |  |  | RPC Operation | BP-11/13 , HP24/36
| 179 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 180 | Lahore | Verify RPC action | 2xHP12/24
| 181 | Matiari |  | BP-11/13 , HP24/36
| 182 | Lahore | Make sure PCP-A is active Simulate Pole1 a DC Line Fault by activating the DC line protection in PCPA
| 183 | Lahore | Verify the firing angle has been retarded in Lahore station
| 184 | Matiari/ Lahore | Verify that pole1 quickly recovers within the expected time delays.
| 185 | Lahore | Change all the modified settings back to original value.
Simulated Pole2 DC Line Fault (only Lahore) (Sr. No. 34) (A4 12.3.4) | 186 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 187 |  | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 188 | Lahore | Start the BIPOLE | Power | 400 MW
| 189 |  |  | Ramp Rate: | 50 MW/Min
| 190 |  | Wait to achieve Target Value | Max Time | 5 min
| 191 | Lahore | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 192 |  |  | DC Voltages | ±660kV
| 193 |  |  | RPC Operation | 2xHP12/24
| 194 | Matiari |  | Extinction Angle (g) | 17°
| 195 |  |  | DC Voltages | Range to be mentioned
| 196 |  |  | RPC Operation | BP-11/13 , HP24/36
| 197 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 198 | Lahore | Verify RPC action | 2xHP12/24
| 199 | Matiari |  | BP-11/13 , HP24/36
| 200 | Lahore | Make sure PCP-A is active Simulate Pole2 a DC Line Fault by activating the DC line protection in PCPA
| 201 | Lahore | Verify the firing angle has been retarded in Lahore station
| 202 | Matiari/ Lahore | Verify that pole2 quickly recovers within the expected time delays.
| 203 | Lahore | Change all the modified settings back to original value.
Test Acceptance Criteria | 204 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 205 |  | All Operations executed successfully
| 206 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 207 |  | All thyristor check-back signals are available.
| 208 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 209 |  | Measuring quantities are available and the values are within the specified range and phase.
| 210 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 211 |  | No Stuck Condition
| 212 |  | No False Tripping by DC Protection System
| 213 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 214 |  | No Tripping in AC side of converter Station

## ACDCFault
Condition
13-AC/DC Line Faults Joint Power Control, Bi-Pole Ground Return
Test Objective | The test objective is to check DC control and protection system function during the DC line fault.
Condition | Sr. No. | Station | Action | Equipment/ Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side at Matiari C/S | Both Poles will operate in Bipole Ground Return Mode see Status Table "BP-GR" |  |  | BI-Pole Mode of Operation
| 4 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 5 |  | All the Prerequisites as mentioned in DC Dispatch Plan should be met.
| 6 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 7 |  | All electrical connections are available.
| 8 |  | Protection settings and protective circuits trip sequences tests must be completed.
| 9 |  | AC-switchyard and associated protections and sequences, including breaker failure protection, must be active.
| 10 |  | Correct grounding of all equipment is available.
| 11 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 12 |  | Thyristor valves and valve hall is cleaned.
| 13 |  | Converter transformers are demagnetized.
| 14 |  | Air humidity and temperature in valve hall are within expected limits.
| 15 |  | Pole Compensation and disturbance test, Reversed Power Direction (Annex-D-XII must be successful)
| 16 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (400 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 17 |  | Confirm DC line restart function is enabled
| 18 |  | NTDC authority approval required before conducting AC Fault Tests (Optional)
| 19 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 20 |  | Return | Ground |  | Ground Return Mode
| 21 |  | Udc Mode | Normal |  | ±660 kV
| 22 |  | Telecom Mode | Operational
| 23 |  | Master Station | Matiari
| 24 | Configuration Setting at Matiari & Lahore C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 25 |  |  | B | Standby
| 26 |  | Pole Control Protection (PCP) | A | ACTIVE
| 27 |  |  | B | Standby
| 28 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 29 |  | Station Control Mode | Joint | ACTIVE | Matiari & Lahore will operate jointly.
| 30 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 31 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
DC Line Faults at Pole 1 near Rectifier, Normal Power Direction (Sr. No. 35) (A4 13.3.1) | 32 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 33 |  | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 34 | Matiari & Lahore | Start the BIPOLE | Power | 400 MW
| 35 |  |  | Ramp Rate: | 50 MW/Min
| 36 |  | Wait to achieve Target Value | Max Time | 5 min
| 37 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 38 |  |  | DC Voltages | ±660 kV
| 39 |  |  | RPC Operation | BP-11/13 , HP24/36
| 40 | Lahore |  | Extinction Angle (g) | 17°
| 41 |  |  | DC Voltages | Range to be mentioned
| 42 |  |  | RPC Operation | 2xHP12/24
| 43 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 44 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 45 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 46 | Lahore |  | 2xHP12/24
| 47 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 48 | Matiari | DC Line Faults at Pole 1 near Rectifier should be initiated in line with the guidance in DC Line Faults Tests Program.
| 49 | Lahore/ Matiari | Verify | DC line traveling wave protection and derivative protection operated
| 50 |  |  | Order down in rectifier from DC line protections.
| 51 |  |  | DC line successfully restarted to full voltage on first attempt
| 52 |  |  | The actual distance would be same as that shown on the LFL indication
Pole 2 Reduced Voltage, DC Line Faults at Pole 2 near Rectifier, Normal Power Direction (Sr. No. 36) (A4 13.3.2) | 53 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 54 | Matiari & Lahore | Start the BiPole | Power | 400 MW
| 55 |  |  | Ramp Rate: | 50 MW/Min
| 56 |  | Wait to achieve Target Value | Max Time | 5 min
| 57 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 58 |  |  | DC Voltages | ±660 kV
| 59 |  |  | RPC Operation | BP-11/13 , HP24/36
| 60 | Lahore |  | Extinction Angle (g) | 17°
| 61 |  |  | DC Voltages | Range to be mentioned
| 62 |  |  | RPC Operation | 2xHP12/24
| 63 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 64 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 65 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 66 | Lahore |  | 2xHP12/24
| 67 | Matiari | Order pole 2 in REDUCED VOLTAGE (70% of nominal voltage).
| 68 |  | Verify dc voltage ramps down to 70% (462kV)
| 69 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 70 | Matiari | DC Line Faults at Pole 2 near Rectifier should be initiated in line with the guidance in DC Line Faults Tests Program.
| 71 | Matiari/Lahore | Verify | DC line traveling wave protection and derivative protection operated
| 72 |  |  | Order down in rectifier from DC line protections.
| 73 |  |  | DC line successfully restarted to pre-disturbance reduced voltage on first attempt
| 74 |  |  | The actual distance would be same as that shown on the LFL indication
DC Line Faults at Pole 1 near Inverter, Normal Power Direction (Sr. No. 37) (A4 13.3.3) | 75 | Matiari | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 76 | Matiari & Lahore | Start the BIPOLE | Power | 400 MW
| 77 |  |  | Ramp Rate: | 50 MW/Min
| 78 |  | Wait to achieve Target Value | Max Time | 5 min
| 79 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 80 |  |  | DC Voltages | ±660 kV
| 81 |  |  | RPC Operation | BP-11/13 , HP24/36
| 82 | Lahore |  | Extinction Angle (g) | 17°
| 83 |  |  | DC Voltages | Range to be mentioned
| 84 |  |  | RPC Operation | 2xHP12/24
| 85 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 86 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 87 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 88 | Lahore |  | 2xHP12/24
| 89 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 90 | Lahore | DC Line Faults at Pole 1 near Inverter should be initiated in line with the guidance in DC Line Faults Tests Program.
| 91 | Lahore/ Matiari | Verify | DC line traveling wave protection and derivative protection operated
| 92 |  |  | Order down in rectifier from DC line protections.
| 93 |  |  | DC line successfully restarted to full voltage on first attempt
| 94 |  |  | The actual distance would be same as that shown on the LFL indication
Pole 1 Reduced Voltage, DC Line Faults at Pole 1 near Inverter, Normal Power Direction (Sr. No. 38) (A4 13.3.4) | 95 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 96 | Matiari | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 97 | Matiari & Lahore | Start the BiPole, | Power | 400 MW
| 98 |  |  | Ramp Rate: | 50 MW/Min
| 99 |  | Wait to achieve Target Value | Max Time | 5 min
| 100 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 101 |  |  | DC Voltages | ±660 kV
| 102 |  |  | RPC Operation | BP-11/13 , HP24/36
| 103 | Lahore |  | Extinction Angle (g) | 17°
| 104 |  |  | DC Voltages | Range to be mentioned
| 105 |  |  | RPC Operation | 2xHP12/24
| 106 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 107 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 108 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 109 | Lahore |  | 2xHP12/24
| 110 | Matiari/Lahore | Order pole 1 in REDUCED VOLTAGE (70% of nominal voltage-462 kV).
| 111 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 112 | Lahore | DC Line Faults at Pole 1 near Inverter with the guidance in DC Line Faults Tests Program.
| 113 | Matiari/Lahore | Verify | DC line traveling wave protection and derivative protection operated
| 114 |  |  | Order down in rectifier from DC line protections.
| 115 |  |  | DC line successfully restarted to pre-disturbance reduced voltage on first attempt
| 116 |  |  | The actual distance would be same as that shown on the LFL indication
Pole 1 Reduced Voltage, DC Line Faults at Pole 2 near Inverter, Normal Power Direction (Sr. No. 39) (A4 13.3.5) | 117 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 118 | Matiari | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 119 | Matiari & Lahore | Start the BiPole, | Power | 400 MW
| 120 |  |  | Ramp Rate: | 50 MW/Min
| 121 |  | Wait to achieve Target Value | Max Time | 5 min
| 122 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 123 |  |  | DC Voltages | ±660 kV
| 124 |  |  | RPC Operation | BP-11/13 , HP24/36
| 125 | Lahore |  | Extinction Angle (g) | 17°
| 126 |  |  | DC Voltages | Range to be mentioned
| 127 |  |  | RPC Operation | 2xHP12/24
| 128 | Matiari/Lahore | Verify stable operation & Normal start at reduced power
| 129 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 130 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 131 | Lahore |  | 2xHP12/24
| 132 | Matiari/Lahore | Order pole 1 in REDUCED VOLTAGE (70% of nominal voltage 462kV).
| 133 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 134 | Lahore | DC Line Faults at Pole 2 near Inverter with the guidance in DC Line Faults Tests Program.
| 135 | Matiari/Lahore | Verify | DC line traveling wave protection and derivative protection operated
| 136 |  |  | Order down in rectifier from DC line protections.
| 137 |  |  | DC line successfully restarted to full voltage on first attempt
| 138 |  |  | The actual distance would be same as that shown on the LFL indication
DC Line Faults at Pole 2 near Inverter, Metallic Return Operation, Normal Power Direction (Sr. No. 40) (A4 13.3.6) | 139 | Matiari/Lahore C/S DC side | Order pole 2 TRANSFER TO METALLIC RETURN
| 140 |  | Verify Ready for Operation Conditions.
| 141 | Matiari & Lahore | Start the BiPole, | Power | 200 MW
| 142 |  |  | Ramp Rate: | 50 MW/Min
| 143 |  | Wait to achieve Target Value | Max Time | 5 min
| 144 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 145 |  |  | DC Voltages | -660 kV
| 146 |  |  | RPC Operation | BP-11/13 , HP24/36
| 147 | Lahore |  | Extinction Angle (g) | 17°
| 148 |  |  | DC Voltages | Range to be mentioned
| 149 |  |  | RPC Operation | 2xHP12/24
| 150 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 151 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 152 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 153 | Lahore |  | 2xHP12/24
| 154 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 155 | Lahore | DC Line Faults at Pole 2 near Inverter with the guidance in DC Line Faults Tests Program.
| 156 | Matiari/Lahore | Verify | DC line traveling wave protection and derivative protection operated
| 157 |  |  | Order down in rectifier from DC line protections.
| 158 |  |  | DC line successfully restarted to full voltage on first attempt
| 159 |  |  | The actual distance would be same as that shown on the LFL indication
Fault in Pole 2 at neutral connection, with Pole-I running at 200 MW.(See Figure Below) (Sr. No. 41) | 160 | Matiari/Lahore | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 161 | Matiari & Lahore | Start the Pole 1 | Power | 400 MW
| 162 |  |  | Ramp Rate: | 50 MW/Min
| 163 |  | Wait to achieve Target Value | Max Time | 5 min
| 164 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 165 |  |  | DC Voltages | +660 kV
| 166 |  |  | RPC Operation | BP-11/13 , HP24/36
| 167 | Lahore |  | Extinction Angle (g) | 17°
| 168 |  |  | DC Voltages | Range to be mentioned
| 169 |  |  | RPC Operation | 2xHP12/24
| 170 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 171 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 172 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 173 | Lahore |  | 2xHP12/24
| 174 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 175 | Matiari/Lahore | Apply solid fault in pole 2 on the neutral bus on the valve side of the neutral bus smoothing reactor as per attached one line diagram.
| 176 | Matiari | Connect but Do Not Start/Deblock Pole 2
| 177 | Lahore/ Matiari | Verify | Pole 2 -Pole differential protection operates and causes the Pole 2 to isolate by opening the Pole 2 NBS followed by opening the Pole 2 DC line disconnect switch.
| 178 |  |  | Pole 2 -Pole differential protection operates. Bipole neutral differential protection does not operate. Pole 1 - Pole differential protection does not trip Pole 1 - converter transformer does not trip due to saturation (over fluxing protection).
| 179 |  |  | Initiate a TFR manual trigger when the operator issues the Pole 2 connect command to ensure that signals are captured.
| 180 |  |  | Collect and save all data records.
DC Line Faults at Pole 1 near Rectifier, Reverse Power Direction (Optional) (Sr. No. 42) | 181 | Matiari/Lahore | Verify Reverse Power Direction mode
| 182 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 183 |  | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 184 | Matiari & Lahore | Start the BIPOLE | Power | 400 MW
| 185 |  |  | Ramp Rate: | 50 MW/Min
| 186 |  | Wait to achieve Target Value | Max Time | 5 min
| 187 | Lahore | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 188 |  |  | DC Voltages | ±660 kV
| 189 |  |  | RPC Operation | 2xHP12/24
| 190 | Matiari |  | Extinction Angle (g) | 17°
| 191 |  |  | DC Voltages | Range to be mentioned
| 192 |  |  | RPC Operation | BP-11/13, HP-24/36
| 193 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 194 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 195 | Lahore | Verify RPC action | 2xHP 12/24
| 196 | Matiari |  | BP-11/13, HP-24/36
| 197 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 198 | Lahore | DC Line Faults at Pole 1 near Rectifier should be initiated in line with the guidance in DC Line Faults Tests Program.
| 199 | Lahore/ Matiari | Verify | DC line traveling wave protection and derivative protection operated
| 200 |  |  | Order down in rectifier from DC line protections.
| 201 |  |  | DC line successfully restarted to full voltage on first attempt
| 202 |  |  | The actual distance would be same as that shown on the LFL indication
DC Line Faults at Pole 2 near Inverter, Reverse Power Direction (Optional) (Sr. No. 43) | 203 | Matiari/Lahore | Verify Reverse Power Direction mode
| 204 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 205 |  | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 206 | Matiari & Lahore | Start the BIPOLE | Power | 400 MW
| 207 |  |  | Ramp Rate: | 50 MW/Min
| 208 |  | Wait to achieve Target Value | Max Time | 5 min
| 209 | Lahore | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 210 |  |  | DC Voltages | ±660 kV
| 211 |  |  | RPC Operation | 2xHP12/24
| 212 | Matiari |  | Extinction Angle (g) | 17°
| 213 |  |  | DC Voltages | Range to be mentioned
| 214 |  |  | RPC Operation | BP-11/13, HP-24/36
| 215 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 216 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 217 | Lahore | Verify RPC action | 2xHP 12/24
| 218 | Matiari |  | BP-11/13, HP-24/36
| 219 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 220 | Matiari | DC Line Faults at Pole 2 near Inverter should be initiated in line with the guidance in DC Line Faults Tests Program.
| 221 | Lahore/ Matiari | Verify | DC line traveling wave protection and derivative protection operated
| 222 |  |  | Order down in rectifier from DC line protections.
| 223 |  |  | DC line successfully restarted to full voltage on first attempt
| 224 |  |  | The actual distance would be same as that shown on the LFL indication
AC Line Faults at Rectifier, Normal Power Direction (Optional) (Sr. No. 44) (A4 13.3.7) | 225 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 226 |  | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 227 | Matiari & Lahore | Start the BiPole, | Power | 400 MW
| 228 |  |  | Ramp Rate: | 50 MW/Min
| 229 |  | Wait to achieve Target Value | Max Time | 5 min
| 230 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 231 |  |  | DC Voltages | ±660 kV
| 232 |  |  | RPC Operation | BP-11/13 , HP24/36
| 233 | Lahore |  | Extinction Angle (g) | 17°
| 234 |  |  | DC Voltages | Range to be mentioned
| 235 |  |  | RPC Operation | 2xHP12/24
| 236 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 237 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 238 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 239 | Lahore |  | 2xHP12/24
| 240 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 241 | Matiari | AC Line Faults at Rectifier should be initiated in line with the guidance in AC Line Faults Tests Program.
| 242 | Matiari/Lahore | Verify | Low AC voltage at rectifier is detected. TFR operates to record dc system performance during fault and recovery.
| 243 |  |  | DC system restores to normal operation after the clearance of AC line fault.
AC Line Faults at Invert er, Normal Power Direction (Optional) (Sr. No. 45) | 244 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 245 |  | Verify Pole-I and Pole-II is in Bi-Pole Power Control Mode.
| 246 | Matiari & Lahore | Start the BiPole, | Power | 400 MW
| 247 |  |  | Ramp Rate: | 50 MW/Min
| 248 |  | Wait to achieve Target Value | Max Time | 5 min
| 249 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 250 |  |  | DC Voltages | ±660 kV
| 251 |  |  | RPC Operation | BP-11/13 , HP24/36
| 252 | Lahore |  | Extinction Angle (g) | 17°
| 253 |  |  | DC Voltages | Range to be mentioned
| 254 |  |  | RPC Operation | 2xHP12/24
| 255 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 256 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 257 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 258 | Lahore |  | 2xHP12/24
| 259 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 400 MW with DC System. (Sudden load sharing from DC corridor to AC corridor can happen in next step in case of DC system failure)
| 260 | Lahore | AC Line Faults at Inverter should be initiated in line with the guidance in AC Line Faults Tests Program.
| 261 | Matiari/Lahore | Verify | Low AC voltage at rectifier is detected.
| 262 |  |  | Commutation failure occurs.
| 263 |  |  | DC system restores to normal operation after the clearance of AC line fault.
Test Acceptance Criteria | 264 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 265 |  | All Operations executed successfully
| 266 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 267 |  | All thyristor check-back signals are available.
| 268 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 269 |  | Measuring quantities are available and the values are within the specified range and phase.
| 270 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 271 |  | No Stuck Condition
| 272 |  | No False Tripping by DC Protection System
| 273 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power, current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 274 |  | No Tripping in AC side of converter Station
Figure related to test at Sr. No. 41

## Status Table A
Status Tables-A
Note O/C indcates postion can be open or closed
Reference names |  |  | P1-MR | P2-MR | P1-GR | P2-GR | P1-ISOLAT | P2-ISOLAT | Mat-P1-GR |  | Mat-P2-GR |  | Mat-DCY-Main
Reference names |  |  | Mat-P1-MR | Mat-P2-MR | Mat-P1-GR | Mat-P2-GR | Mat-P1-ISOLAT | Mat-P2-ISOLAT
|  |  | Metallic Return - Pole 1 | Metallic Return - Pole 2 | Ground Return - Pole 1 | Ground Return - Pole 2 | Isolation Mode-Pole 1 | Isolation Mode-Pole 2 | Maintenance Mode - Pole 1 (With DC line) | Maintenance Mode - Pole 1 (Without DC line) | Maintenance Mode - Pole 2 (With DC line) | Maintenance Mode - Pole 2 (Without DC line) | Maintnance Mode - DC Yard
Matiari - Pole 1
1 | Valve Hall | U1E1 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
2 |  | U1E2 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
3 |  | U1E3 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
4 |  | U1E4 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
5 | Pole-I | WN1Q1(NBS) | CLOSED | O/C | CLOSED | O/C | OPEN | O/C | OPEN | OPEN | O/C | O/C | OPEN
6 |  | WN1Q11 | CLOSED | OPEN | CLOSED | OPEN | OPEN | O/C | OPEN | OPEN | O/C | O/C | OPEN
7 |  | WN1Q12 | CLOSED | OPEN | CLOSED | OPEN | OPEN | O/C | OPEN | OPEN | O/C | O/C | OPEN
8 |  | WP1Q11 | CLOSED | OPEN | CLOSED | O/C | OPEN | OPEN | OPEN | OPEN | O/C | O/C | OPEN
9 |  | WP1Q10 | OPEN | CLOSED | OPEN | OPEN | O/C | OPEN | OPEN | CLOSED | O/C | O/C | OPEN
10 |  | P1E11 | OPEN | OPEN | OPEN | O/C | OPEN | O/C | CLOSED | OPEN | O/C | O/C | CLOSED
11 |  | P1E12 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
12 |  | N1E11 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
13 |  | N1E12 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
14 | DC Filters | WF1Q11 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
15 |  | WF1Q12 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
16 |  | WF1Q13 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
17 |  | WF1Q14 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
18 |  | F1E11 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
19 |  | F1E12 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
20 |  | F1E13 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
21 |  | F1E14 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
Matiari - Pole 2
1 | Valve Hall | U2E1 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
2 |  | U2E2 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
3 |  | U2E3 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
4 |  | U2E4 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
5 | Pole-II | WN2Q1(NBS) | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
6 |  | WN2Q11 | OPEN | CLOSED | OPEN | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
7 |  | WN2Q12 | OPEN | CLOSED | OPEN | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
8 |  | WP2Q11 | OPEN | CLOSED | O/C | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
9 |  | WP2Q10 | CLOSED | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | OPEN | CLOSED | OPEN
10 |  | P2E11 | OPEN | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | OPEN | CLOSED
11 |  | P2E12 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
12 |  | N2E11 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
13 |  | N2E12 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
14 | DC Filters | WF2Q11 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
15 |  | WF2Q12 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
16 |  | WF2Q13 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
17 |  | WF2Q14 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
18 |  | F2E11 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
19 |  | F2E12 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
20 |  | F2E13 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
21 |  | F2E14 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
Matiari - Common
1 | NBGS | WGQ1 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | OPEN
2 |  | WGQ10 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
3 |  | WNQ12 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
4 | MRTB | WN3Q1 | OPEN | OPEN | CLOSED | CLOSED | O/C | O/C | O/C | O/C | O/C | O/C | OPEN
5 |  | WN3Q11 | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | O/C | O/C | OPEN
6 |  | WN3Q12 | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | O/C | O/C | OPEN
7 |  | WN3Q13 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | OPEN
8 |  | N3E11 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
9 |  | N3E12 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
10 | GRTS | WNQ1 | CLOSED | CLOSED | OPEN | OPEN | O/C | O/C | O/C | O/C | O/C | O/C | OPEN
11 |  | WNQ11 | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | O/C | O/C | OPEN
12 |  | NE11 | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | O/C | O/C | CLOSED
13 |  | NE12 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
14 | Electrode Station | WEQ11 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
15 |  | WEQ12 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
16 |  | EE-11 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
17 |  | EE-12 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
Reference names |  |  | Lah-P1-MR | Lah-P2-MR | Lah-P1-GR | Lah-P2-GR | Lah-P1-ISOLAT | Lah-P2-ISOLAT
|  |  | Metallic Return - Pole 1 | Metallic Return - Pole 2 | Ground Return - Pole 1 | Ground Return - Pole 2 |  |  | Maintenance Mode - Pole 1 (With DC line) |  | Maintenance Mode - Pole 2 (With DC line) |  | Maintnance Mode - DC Yard
Lahore Pole 1
1 | Valve Hall | U1E1 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
2 |  | U1E2 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
3 |  | U1E3 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
4 |  | U1E4 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
5 | Pole-I | WN1Q1(NBS) | CLOSED | O/C | CLOSED | O/C | OPEN | O/C | OPEN | OPEN | O/C | O/C | OPEN
6 |  | WN1Q11 | CLOSED | OPEN | CLOSED | OPEN | OPEN | O/C | OPEN | OPEN | O/C | O/C | OPEN
7 |  | WN1Q12 | CLOSED | OPEN | CLOSED | OPEN | OPEN | O/C | OPEN | OPEN | O/C | O/C | OPEN
8 |  | WP1Q11 | CLOSED | OPEN | CLOSED | O/C | OPEN | O/C | OPEN | OPEN | O/C | O/C | OPEN
9 |  | WP1Q10 | OPEN | CLOSED | OPEN | OPEN | O/C | OPEN | OPEN | CLOSED | O/C | O/C | OPEN
10 |  | P1E11 | OPEN | OPEN | OPEN | O/C | OPEN | O/C | CLOSED | OPEN | O/C | O/C | CLOSED
11 |  | P1E12 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
12 |  | N1E11 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
13 |  | N1E12 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
14 | DC Filters | WF1Q11 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
15 |  | WF1Q12 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
16 |  | WF1Q13 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
17 |  | WF1Q14 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
18 |  | F1E11 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
19 |  | F1E12 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
20 |  | F1E13 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
21 |  | F1E14 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
Lahore Pole 2
1 | Valve Hall | U2E1 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
2 |  | U2E2 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
3 |  | U2E3 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
4 |  | U2E4 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
5 | Pole-II | WN2Q1(NBS) | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
6 |  | WN2Q11 | OPEN | CLOSED | OPEN | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
7 |  | WN2Q12 | OPEN | CLOSED | OPEN | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
8 |  | WP2Q11 | OPEN | CLOSED | O/C | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
9 |  | WP2Q10 | CLOSED | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | OPEN | CLOSED | OPEN
10 |  | P2E11 | OPEN | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | OPEN | CLOSED
11 |  | P2E12 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
12 |  | N2E11 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
13 |  | N2E12 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
14 | DC Filters | WF2Q11 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
15 |  | WF2Q12 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
16 |  | WF2Q13 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
17 |  | WF2Q14 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
18 |  | F2E11 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
19 |  | F2E12 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
20 |  | F2E13 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
21 |  | F2E14 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
Lahore Common Neutral
1 | NBGS | WGQ1 [NBGS] | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | OPEN
2 |  | WNQ12 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
3 |  | WGQ10 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
4 | MRTB (Metallic Return Transfer Bus) | WN3Q11 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
5 |  | N3E11 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
6 |  | N3E12 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
7 | GRTS(Ground Return Transfer Switch) | WNQ11 | CLOSED | CLOSED | OPEN | OPEN | O/C | O/C | O/C | O/C | O/C | O/C | OPEN
8 |  | NE11 | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | O/C | O/C | CLOSED
9 |  | NE12 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
10 | Electrode Station | WEQ11 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
11 |  | WEQ12 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
12 |  | EE-11 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
13 |  | EE-12 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED

## Status Table B
Status Tables-B
Ready For Energization
These condition must be met before energizing C/T/F
1 | Valve Hall Locked
2 | Valve Hall Man Door Closed
3 | Valve Cooling is Ok and Running
4 | NO Emergency Stop Orders (ESOF)
5 | Ground Switches Open at AC side
6 | Ground Switches Open at DC side
Ready For Operation
These Conditions must be met before Deblocking the Valve
1 | No Emergency Fault
2 | No Protectiion Trip Orders
3 | Tap Changer Ready
4 | Pole Connected
5 | Valve Energized
6 | Valve Blocked
7 | System/Station level control selected
8 | Power Direction Selected
9 | No inhibit SigO/Cl from measuring Devices.
Pre-condition | Pole-1 is isolated
Switch Operation Sequence | Transfer from Pole 2 GR to Pole 2 MR on Pole 1 Conductor
| Matiari CS |  | Lahore CS
1 | NE11 | OPEN | NE11 | OPEN
2 | WNQ11 | CLOSED | WNQ11 | CLOSED
3 | WP2Q10 | CLOSED | WP2Q10 | CLOSED
4 | WNQ1(GRTS) | CLOSED | / | /
5 | WN3Q1(MRTB) | OPEN | / | /
6 | WN3Q11 | OPEN | / | /
7 | WN3Q12 | OPEN | / | /
Pre-condition | Pole-1 is isolated
Switch Operation Sequence | Transfer from Pole 2 MR on Pole 1 conductor to Pole 2 GR
| Matiari CS |  | Lahore CS
1 | WN3Q11 | CLOSED | / | /
2 | WN3Q12 | CLOSED | / | /
3 | WN3Q1(MRTB) | CLOSED | / | /
4 | WNQ1(GRTS) | OPEN | / | /
5 | WP2Q10 | OPEN | WP2Q10 | OPEN
6 | WNQ11 | OPEN | WNQ11 | OPEN
7 | NE11 | CLOSED | NE11 | CLOSED
Pre-condition | Pole-2 is isolated
Switch Operation Sequence | Transfer from GR to MR on Pole 2 Conductor
| Matiari CS |  | Lahore CS
1 | NE11 | OPEN | NE11 | OPEN
2 | WNQ11 | CLOSED | WNQ11 | CLOSED
3 | WP1Q10 | CLOSED | WP1Q10 | CLOSED
4 | WNQ1(GRTS) | CLOSED | / | /
5 | WN3Q1(MRTB) | OPEN | / | /
6 | WN3Q11 | OPEN | / | /
7 | WN3Q12 | OPEN | / | /
Pre-condition | Pole-2 is isolated
Switch Operation Sequence | Transfer from MR on Pole 2 conductor to GR
| Matiari CS |  | Lahore CS
1 | WN3Q11 | CLOSED | / | /
2 | WN3Q12 | CLOSED | / | /
3 | WN3Q1(MRTB) | CLOSED | / | /
4 | WNQ1(GRTS) | OPEN | / | /
5 | WP1Q10 | OPEN | WP1Q10 | OPEN
6 | WNQ11 | OPEN | WNQ11 | OPEN
7 | NE11 | CLOSED | NE11 | CLOSED
Switch Operation Sequence | Transfer from BPGR to MR Pole-1 on Pole 2 Conductor
The sequnce of transition is:
1 | BPGR ==>Stop or Block Pole1
2 | Stop or Block Pole1==> Monopolar GR Pole 2
3 | Monopolar GR Pole 2==> Isolate Pole 1
4 | Isolate Pole 1==>Pole1 Isolated Both Stations
5 | Pole1 Isolated Both Stations==>P2 GR to Metallic Return on Pole 1 Conductor
Switch Operation Sequence | Transfer from BPGR to MR Pole-2 On Pole 1 Conductor
The sequnce of transition is:
1 | BPGR ==>Stop or Block Pole 2
2 | Stop or Block Pole 2==> Monopolar GR Pole 1==>Isolate Pole 2
3 | Monopolar GR Pole 1==>Isolate Pole 2
4 | Isolate Pole 2==> Pole2 Isolated Both Stations
5 | Pole2 Isolated Both Stations==>P1 GR to Metallic Return on Pole 2 Conductor
Switch Operation Sequence | Transfer from MR Pole-1 on Pole 2 Conductor to BPGR
The sequnce of transition is:
1 | MR Pole 1 ==> GR Pole 1
2 | GR Pole 1==> Pole 2 is Isolated
3 | Pole 2 is Isolated==> Connect Pole 2 both stations
4 | Connect Pole 2 both stations==>Start Pole2
Switch Operation Sequence | Transfer from MR Pole-2 on Pole 1 Conductor to BPGR
The sequnce of transition is:
1 | MR Pole 2==> GR Pole 2
2 | GR Pole 2==> Pole 1 is Isolated
3 | Pole 1 is Isolated==> Connect Pole 1 both stations
4 | Connect Pole 1 both stations==>Start Pole 1
Switch Operation Sequence | Transfer from BPGR to GR Pole-1
This transition happens automatically when Pole 2 is blocked or tripped, the sequence is:
1 | Stop or trip pole 2 ==> Isolate Pole 2
2 | Isolate Pole 2==> Pole 2 is Isolated
Switch Operation Sequence | Transfer from BPGR to GR Pole-2
This transition happens automatically when Pole 1 is blocked or tripped, the sequence is:
1 | Stop or trip pole 1 ==> Isolate Pole 1
2 | Isolate Pole 1==> Pole 1 is Isolated
Switch Operation Sequence | Transfer from GR Pole-1 to BPGR
This transition happens when you connect and start Pole2 when Pole 1 is already running in GR, The sequence is:
1 | Pole 2 is isolated==> Connect Pole 2==>Pole 2 is connected
2 | Connect Pole 2==>Pole 2 is connected
3 | Pole 2 is connected ==>Start Pole 2 (now in BPGR)
Switch Operation Sequence | Transfer from GR Pole-2 to BPGR
This transition happens when you connect and start Pole 1 when Pole 2 is already running in GR, The sequence is:
1 | Pole 1 is isolated==> Connect Pole 1
2 | Connect Pole 1==>Pole 1 is connected
3 | Pole 1 is connected ==>Start Pole 1 (now in BPGR)
Switch Operation Sequence | Start Pole
The sequnce of transition is:
1 | Open Valve Hall Grounding Switches
2 | when the first switch is opened, the sequence will open the next one and so on.
3 | Pole Connect
4 | Connect DC Filter
Switch Operation Sequence | Stop Pole
The sequnce of transition is:
1 | Close Valve Hall Grounding Switches
2 | when the close indication has reached the first switch, the sequence will close the next one and so on.
3 | Pole Disconnect
4 | Disconnect DC Filter
Switch Operation Sequence | Pole Connect
The sequnce of transition is:
1 | Close the disconnector(WNQ11)
2 | Close the ground return neutral bus disconnector
3 | Close the metallic return neutral bus disconnector
4 | Close the neutral bus switch (WNQ1)
5 | Close the pole line disconnector (WPxQ11), x=1 or 2 depending on Pole1 or Pole respectively
6 | Pole is Connected
Switch Operation Sequence | Pole Isolate
The sequnce of transition is:
1 | Open the pole line disconnector (WPxQ11), x=1 or 2 depending on Pole1 or Pole respectively
2 | When UDL voltage is low, open the neutral bus switch
3 | Open the ground return disconnector
4 | Open the metallic return neutral bus disconnector
5 | Pole is isolated