## Status Table A
Status Tables
Note O/C indcates postion can be open or closed
Reference names |  |  | P1-MR | P2-MR | P1-GR | P2-GR | P1-ISOLAT | P2-ISOLAT | Mat-P1-GR |  | Mat-P2-GR |  | Mat-DCY-Main
Reference names |  |  | Mat-P1-MR | Mat-P2-MR | Mat-P1-GR | Mat-P2-GR | Mat-P1-ISOLAT | Mat-P2-ISOLAT
|  |  | Metallic Return - Pole 1 | Metallic Return - Pole 2 | Ground Return - Pole 1 | Ground Return - Pole 2 | Isolation Mode-Pole 1 | Isolation Mode-Pole 2 | Maintenance Mode - Pole 1 (With DC line) | Maintenance Mode - Pole 1 (Without DC line) | Maintenance Mode - Pole 2 (With DC line) | Maintenance Mode - Pole 2 (Without DC line) | Maintnance Mode - DC Yard
Matiari - Pole 1
1 | Valve Hall | U1E1 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
2 |  | U1E2 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
3 |  | U1E3 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
4 |  | U1E4 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
5 | Pole-I | WN1Q1(NBS) | CLOSED | O/C | CLOSED | O/C | OPEN | O/C | OPEN | OPEN | O/C | O/C | OPEN
6 |  | WN1Q11 | CLOSED | OPEN | CLOSED | OPEN | OPEN | O/C | OPEN | OPEN | O/C | O/C | OPEN
7 |  | WN1Q12 | CLOSED | OPEN | CLOSED | OPEN | OPEN | O/C | OPEN | OPEN | O/C | O/C | OPEN
8 |  | WP1Q11 | CLOSED | OPEN | CLOSED | O/C | OPEN | OPEN | OPEN | OPEN | O/C | O/C | OPEN
9 |  | WP1Q10 | OPEN | CLOSED | OPEN | OPEN | O/C | OPEN | OPEN | CLOSED | O/C | O/C | OPEN
10 |  | P1E11 | OPEN | OPEN | OPEN | O/C | OPEN | O/C | CLOSED | OPEN | O/C | O/C | CLOSED
11 |  | P1E12 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
12 |  | N1E11 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
13 |  | N1E12 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
14 | DC Filters | WF1Q11 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
15 |  | WF1Q12 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
16 |  | WF1Q13 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
17 |  | WF1Q14 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
18 |  | F1E11 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
19 |  | F1E12 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
20 |  | F1E13 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
21 |  | F1E14 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
Matiari - Pole 2
1 | Valve Hall | U2E1 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
2 |  | U2E2 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
3 |  | U2E3 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
4 |  | U2E4 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
5 | Pole-II | WN2Q1(NBS) | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
6 |  | WN2Q11 | OPEN | CLOSED | OPEN | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
7 |  | WN2Q12 | OPEN | CLOSED | OPEN | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
8 |  | WP2Q11 | OPEN | CLOSED | O/C | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
9 |  | WP2Q10 | CLOSED | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | OPEN | CLOSED | OPEN
10 |  | P2E11 | OPEN | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | OPEN | CLOSED
11 |  | P2E12 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
12 |  | N2E11 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
13 |  | N2E12 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
14 | DC Filters | WF2Q11 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
15 |  | WF2Q12 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
16 |  | WF2Q13 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
17 |  | WF2Q14 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
18 |  | F2E11 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
19 |  | F2E12 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
20 |  | F2E13 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
21 |  | F2E14 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
Matiari - Common
1 | NBGS | WGQ1 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | OPEN
2 |  | WGQ10 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
3 |  | WNQ12 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
4 | MRTB | WN3Q1 | OPEN | OPEN | CLOSED | CLOSED | O/C | O/C | O/C | O/C | O/C | O/C | OPEN
5 |  | WN3Q11 | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | O/C | O/C | OPEN
6 |  | WN3Q12 | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | O/C | O/C | OPEN
7 |  | WN3Q13 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | OPEN
8 |  | N3E11 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
9 |  | N3E12 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
10 | GRTS | WNQ1 | CLOSED | CLOSED | OPEN | OPEN | O/C | O/C | O/C | O/C | O/C | O/C | OPEN
11 |  | WNQ11 | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | O/C | O/C | OPEN
12 |  | NE11 | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | O/C | O/C | CLOSED
13 |  | NE12 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
14 | Electrode Station | WEQ11 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
15 |  | WEQ12 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
16 |  | EE-11 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
17 |  | EE-12 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
Reference names |  |  | Lah-P1-MR | Lah-P2-MR | Lah-P1-GR | Lah-P2-GR | Lah-P1-ISOLAT | Lah-P2-ISOLAT
|  |  | Metallic Return - Pole 1 | Metallic Return - Pole 2 | Ground Return - Pole 1 | Ground Return - Pole 2 |  |  | Maintenance Mode - Pole 1 (With DC line) |  | Maintenance Mode - Pole 2 (With DC line) |  | Maintnance Mode - DC Yard
Lahore Pole 1
1 | Valve Hall | U1E1 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
2 |  | U1E2 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
3 |  | U1E3 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
4 |  | U1E4 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
5 | Pole-I | WN1Q1(NBS) | CLOSED | O/C | CLOSED | O/C | OPEN | O/C | OPEN | OPEN | O/C | O/C | OPEN
6 |  | WN1Q11 | CLOSED | OPEN | CLOSED | OPEN | OPEN | O/C | OPEN | OPEN | O/C | O/C | OPEN
7 |  | WN1Q12 | CLOSED | OPEN | CLOSED | OPEN | OPEN | O/C | OPEN | OPEN | O/C | O/C | OPEN
8 |  | WP1Q11 | CLOSED | OPEN | CLOSED | O/C | OPEN | O/C | OPEN | OPEN | O/C | O/C | OPEN
9 |  | WP1Q10 | OPEN | CLOSED | OPEN | OPEN | O/C | OPEN | OPEN | CLOSED | O/C | O/C | OPEN
10 |  | P1E11 | OPEN | OPEN | OPEN | O/C | OPEN | O/C | CLOSED | OPEN | O/C | O/C | CLOSED
11 |  | P1E12 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
12 |  | N1E11 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
13 |  | N1E12 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
14 | DC Filters | WF1Q11 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
15 |  | WF1Q12 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
16 |  | WF1Q13 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
17 |  | WF1Q14 | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | OPEN | O/C | O/C | OPEN
18 |  | F1E11 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
19 |  | F1E12 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
20 |  | F1E13 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
21 |  | F1E14 | OPEN | O/C | OPEN | O/C | OPEN | O/C | CLOSED | CLOSED | O/C | O/C | CLOSED
Lahore Pole 2
1 | Valve Hall | U2E1 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
2 |  | U2E2 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
3 |  | U2E3 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
4 |  | U2E4 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
5 | Pole-II | WN2Q1(NBS) | O/C | CLOSED | O/C | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
6 |  | WN2Q11 | OPEN | CLOSED | OPEN | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
7 |  | WN2Q12 | OPEN | CLOSED | OPEN | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
8 |  | WP2Q11 | OPEN | CLOSED | O/C | CLOSED | O/C | OPEN | O/C | O/C | OPEN | OPEN | OPEN
9 |  | WP2Q10 | CLOSED | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | OPEN | CLOSED | OPEN
10 |  | P2E11 | OPEN | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | OPEN | CLOSED
11 |  | P2E12 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
12 |  | N2E11 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
13 |  | N2E12 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
14 | DC Filters | WF2Q11 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
15 |  | WF2Q12 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
16 |  | WF2Q13 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
17 |  | WF2Q14 | O/C | CLOSED | O/C | CLOSED | O/C | CLOSED | O/C | O/C | OPEN | OPEN | OPEN
18 |  | F2E11 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
19 |  | F2E12 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
20 |  | F2E13 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
21 |  | F2E14 | O/C | OPEN | O/C | OPEN | O/C | OPEN | O/C | O/C | CLOSED | CLOSED | CLOSED
Lahore Common Neutral
1 | NBGS | WGQ1 [NBGS] | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | OPEN
2 |  | WNQ12 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
3 |  | WGQ10 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
4 | MRTB (Metallic Return Transfer Bus) | WN3Q11 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
5 |  | N3E11 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
6 |  | N3E12 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
7 | GRTS(Ground Return Transfer Switch) | WNQ11 | CLOSED | CLOSED | OPEN | OPEN | O/C | O/C | O/C | O/C | O/C | O/C | OPEN
8 |  | NE11 | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | O/C | O/C | CLOSED
9 |  | NE12 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
10 | Electrode Station | WEQ11 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
11 |  | WEQ12 | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | CLOSED | O/C | O/C | O/C | O/C | OPEN
12 |  | EE-11 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED
13 |  | EE-12 | OPEN | OPEN | OPEN | OPEN | OPEN | OPEN | O/C | O/C | O/C | O/C | CLOSED

## Status Table B
Status Tables
Ready For Energization
These condition must be met before energizing C/T/F
1 | Valve Hall Locked
2 | Valve Hall Man Door Closed
3 | Valve Cooling is Ok and Running
4 | NO Emergency Stop Orders (ESOF)
5 | Ground Switches Open at AC side
6 | Ground Switches Open at DC side
Ready For Operation
These Conditions must be met before Deblocking the Valve
1 | No Emergency Fault
2 | No Protectiion Trip Orders
3 | Tap Changer Ready
4 | Pole Connected
5 | Valve Energized
6 | Valve Blocked
7 | System/Station level control selected
8 | Power Direction Selected
9 | No inhibit SigO/Cl from measuring Devices.
Pre-condition | Pole-1 is isolated
Switch Operation Sequence | Transfer from Pole 2 GR to Pole 2 MR on Pole 1 Conductor
| Matiari CS |  | Lahore CS
1 | NE11 | OPEN | NE11 | OPEN
2 | WNQ11 | CLOSED | WNQ11 | CLOSED
3 | WP2Q10 | CLOSED | WP2Q10 | CLOSED
4 | WNQ1(GRTS) | CLOSED | / | /
5 | WN3Q1(MRTB) | OPEN | / | /
6 | WN3Q11 | OPEN | / | /
7 | WN3Q12 | OPEN | / | /
Pre-condition | Pole-1 is isolated
Switch Operation Sequence | Transfer from Pole 2 MR on Pole 1 conductor to Pole 2 GR
| Matiari CS |  | Lahore CS
1 | WN3Q11 | CLOSED | / | /
2 | WN3Q12 | CLOSED | / | /
3 | WN3Q1(MRTB) | CLOSED | / | /
4 | WNQ1(GRTS) | OPEN | / | /
5 | WP2Q10 | OPEN | WP2Q10 | OPEN
6 | WNQ11 | OPEN | WNQ11 | OPEN
7 | NE11 | CLOSED | NE11 | CLOSED
Pre-condition | Pole-2 is isolated
Switch Operation Sequence | Transfer from GR to MR on Pole 2 Conductor
| Matiari CS |  | Lahore CS
1 | NE11 | OPEN | NE11 | OPEN
2 | WNQ11 | CLOSED | WNQ11 | CLOSED
3 | WP1Q10 | CLOSED | WP1Q10 | CLOSED
4 | WNQ1(GRTS) | CLOSED | / | /
5 | WN3Q1(MRTB) | OPEN | / | /
6 | WN3Q11 | OPEN | / | /
7 | WN3Q12 | OPEN | / | /
Pre-condition | Pole-2 is isolated
Switch Operation Sequence | Transfer from MR on Pole 2 conductor to GR
| Matiari CS |  | Lahore CS
1 | WN3Q11 | CLOSED | / | /
2 | WN3Q12 | CLOSED | / | /
3 | WN3Q1(MRTB) | CLOSED | / | /
4 | WNQ1(GRTS) | OPEN | / | /
5 | WP1Q10 | OPEN | WP1Q10 | OPEN
6 | WNQ11 | OPEN | WNQ11 | OPEN
7 | NE11 | CLOSED | NE11 | CLOSED
Switch Operation Sequence | Transfer from BPGR to MR Pole-1 on Pole 2 Conductor
The sequnce of transition is:
1 | BPGR ==>Stop or Block Pole1
2 | Stop or Block Pole1==> Monopolar GR Pole 2
3 | Monopolar GR Pole 2==> Isolate Pole 1
4 | Isolate Pole 1==>Pole1 Isolated Both Stations
5 | Pole1 Isolated Both Stations==>P2 GR to Metallic Return on Pole 1 Conductor
Switch Operation Sequence | Transfer from BPGR to MR Pole-2 On Pole 1 Conductor
The sequnce of transition is:
1 | BPGR ==>Stop or Block Pole 2
2 | Stop or Block Pole 2==> Monopolar GR Pole 1==>Isolate Pole 2
3 | Monopolar GR Pole 1==>Isolate Pole 2
4 | Isolate Pole 2==> Pole2 Isolated Both Stations
5 | Pole2 Isolated Both Stations==>P1 GR to Metallic Return on Pole 2 Conductor
Switch Operation Sequence | Transfer from MR Pole-1 on Pole 2 Conductor to BPGR
The sequnce of transition is:
1 | MR Pole 1 ==> GR Pole 1
2 | GR Pole 1==> Pole 2 is Isolated
3 | Pole 2 is Isolated==> Connect Pole 2 both stations
4 | Connect Pole 2 both stations==>Start Pole2
Switch Operation Sequence | Transfer from MR Pole-2 on Pole 1 Conductor to BPGR
The sequnce of transition is:
1 | MR Pole 2==> GR Pole 2
2 | GR Pole 2==> Pole 1 is Isolated
3 | Pole 1 is Isolated==> Connect Pole 1 both stations
4 | Connect Pole 1 both stations==>Start Pole 1
Switch Operation Sequence | Transfer from BPGR to GR Pole-1
This transition happens automatically when Pole 2 is blocked or tripped, the sequence is:
1 | Stop or trip pole 2 ==> Isolate Pole 2
2 | Isolate Pole 2==> Pole 2 is Isolated
Switch Operation Sequence | Transfer from BPGR to GR Pole-2
This transition happens automatically when Pole 1 is blocked or tripped, the sequence is:
1 | Stop or trip pole 1 ==> Isolate Pole 1
2 | Isolate Pole 1==> Pole 1 is Isolated
Switch Operation Sequence | Transfer from GR Pole-1 to BPGR
This transition happens when you connect and start Pole2 when Pole 1 is already running in GR, The sequence is:
1 | Pole 2 is isolated==> Connect Pole 2==>Pole 2 is connected
2 | Connect Pole 2==>Pole 2 is connected
3 | Pole 2 is connected ==>Start Pole 2 (now in BPGR)
Switch Operation Sequence | Transfer from GR Pole-2 to BPGR
This transition happens when you connect and start Pole 1 when Pole 2 is already running in GR, The sequence is:
1 | Pole 1 is isolated==> Connect Pole 1
2 | Connect Pole 1==>Pole 1 is connected
3 | Pole 1 is connected ==>Start Pole 1 (now in BPGR)
Switch Operation Sequence | Start Pole
The sequnce of transition is:
1 | Open Valve Hall Grounding Switches
2 | when the first switch is opened, the sequence will open the next one and so on.
3 | Pole Connect
4 | Connect DC Filter
Switch Operation Sequence | Stop Pole
The sequnce of transition is:
1 | Close Valve Hall Grounding Switches
2 | when the close indication has reached the first switch, the sequence will close the next one and so on.
3 | Pole Disconnect
4 | Disconnect DC Filter
Switch Operation Sequence | Pole Connect
The sequnce of transition is:
1 | Close the disconnector(WNQ11)
2 | Close the ground return neutral bus disconnector
3 | Close the metallic return neutral bus disconnector
4 | Close the neutral bus switch (WNQ1)
5 | Close the pole line disconnector (WPxQ11), x=1 or 2 depending on Pole1 or Pole respectively
6 | Pole is Connected
Switch Operation Sequence | Pole Isolate
The sequnce of transition is:
1 | Open the pole line disconnector (WPxQ11), x=1 or 2 depending on Pole1 or Pole respectively
2 | When UDL voltage is low, open the neutral bus switch
3 | Open the ground return disconnector
4 | Open the metallic return neutral bus disconnector
5 | Pole is isolated