## Summary of Converter Transformer Oil Conservator and Dehydrating Breather

Muhammad Shamaas

The XIAN XD Converter Transformer ZZDFPZ-400400/500-660(330) adopts OFAF cooling method. The barrel type oil tank is filled with Petro China KI50X transformer oil. In order to allow the expansion and contraction of transformer oil during temperature changes, the XD China ZX5461.00534 type Oil Conservator is installed. The Transformer breathes air in and out though the MESSKO MTraB DA200D-T Dehydrating Breather.

Converter Transformer Oil Conservator and Dehydrating Breather

- Transformer Breathing

Transformer is an air tight machine completely filled with insulating oil. There is no way to pass air in or out of the transformer. The atmospheric temperature is never constant and oil temperature varies with the loading of transformer. According to themodynamics law, oil expands at high temperature and contracts at low temperature. Hence an outlet is required to requied to adjust the expansion and contraction of Transformer Oil. Some expansion space is provided in the Oil Conservator placed above the Main Oil Tank. The Oil Conservator can exchange air with the atmosphere through the Dehydrating Breather and connection tube.

ZX5461.00534 Oil Conservator

The Transformer always inhales and exhales air during operation through silica gel breathers. When the oil temperature drops, atmospheric air enters the Oil Conservator through the breather to fill the empty space. When the Transformer Oil heats up and expands, air is pushed out through the Breather.

YDA200D-T Dehydrating Breather

- Maintenance of Oil Conservator and Dehydrating Breather

- Oil Level Gauge: Check the upper and lower level limits according to the oil level curve nameplate. The scale and valves must not be rusty. There should be no jamming in the float ball connecting rod installation. Check that the Rotation of bevel gear is normal. Check the oil temperature and pressure during normal breathing. Check the dirt collector for oil stains. Clean the Oil Conservator, rubber bag and replace the oil. Check the seal of the rubber bag for aging or cracks. Conduct gas pressure test for the rubber bag at 0.02-0.03 MPa for 12 hours in a pool to check for leakage of gas or bubbling. If the rubber bag is damaged, it must be replaced. During installation, avoid blockage of connection pipe and joints. Hang the rubber bag on the hook and connect the outlet. Seal the rubber bag nozzle to prevent oil entry. Check safety airways, connection pipe sealing gasket and end cap for firm installation.

- Dehydrating Breather: Check the oil level of oil cup according to the scale indication and check that the oil level breathing oil cup is bubbling. Check the silica gel in the dehydrating breather for signs of moisture. If the blue color changes to 2/3 or more red, the silica gel must be replaced. Check the breather tube and oil seal cup for cracks and damage, blockage, leakage or looseness.

- Gas Relay: Check the exhaust of gas collecting box. The node signal should be normal and there should be no leakage in the metal hose connection.

- Rubber Bag: Check that the Oil level gauge operates normally. There should be no damage during rubber bag inflation inspection. Check that the true oil level is consistent with the oil level indicator.

Tools and consumables 
1 end pressurizing tool with manual hydraulic pump. 
1 grinding tool
Radiator Spreader Block 
Long nose pliers 
1 Thyristor lifting belt
Wrenches
Screwdrivers 
Thyristor Level test instruments and related accessories including grounding cables. 
Anhydrous Alcohol, lint free paper, P600 sandpaper and silicone oil. 

Removal of Thyristor 
1. Disconnect the cable connecting Thyristor gate and TCE.
2. Place the end pressurizing tool on the right end plate of the valve assembly. 
3. Connect the hydraulic pump attached to the spreading tool, pressurize it to the specified value and close the pressure relief valve when applying pressure. 
4. Read the pressure gauge of the hydraulic pump of the end pressurizing tool. 
5. Rotate the clamping nut in the right end plate to the left of the valve assembly until it cannot rotate. Then rotate it back for 1-2 turns. Before rotating, draw a marking line between the clamping nut and the right end plate. 
6. Place two radiator expansion blocks diagonally between radiators on both sides of the fault Thyristor. 
7. Slowly loosen the pressure relief valve on the hand pump connected to the end pressurizing device.
8. Ensure that there is enough distance between radiators (between 38-40 mm) to ensure that the Thyristors can be separated from radiators and replaced.
9. Remove the four fixing screws at the upper clamping band, remove the clamping band and set it aside.
10. Wrap the faulty Thyristor with lifting belt, lifting the belt and then remove the Thyristor.

Insulation Resistance Test 
Requirements: Neutral point Lightning arrester: not less than 2000MOhm, other lightning arrester: not less than 2000MOhm.
Remark: Use Megohmmeter of 2500V and above for neutral point Lightning arrestor.
Use Megohmmeter of 5000V and above for neutral point Lightning arrestor.

Leakage Current Measurement
Requirements: Measure the full current, resistive current or power loss under the operating voltage, and the measured value should not change significantly from the initial value. Compare the measured value with the initial value. When the resistive current increases by 50%, the reason should be analyzed and the monitoring should be strengthened to shorten the detection period appropriately. When the resistive current doubles, the power should be cut off for Inspection.

Remark: The ambient temperature, relative humidity and operating voltage during measurement should be recorded. The live measurement should be carried out when the surface of the arrester housing is dry. Attention should be paid to the inter phase interference. Lightning arresters with full current on line detection devices cannot replace the test of this project. The readings should be recorded regularly. If an abnormality is found, the live or power cut resistive current test should be conducted in time.

Leakage current at 1mA DC U1mA and 0.75U1mA.

Requirements: not less than the value required by the equipment specifications. Compare the measured value of U1mA with its initial value or the value specified by the manufacturer. The difference should not be greater than +-5%. The leakage current at 0.75U1mA should not be greater than 50uA.

Remarks: The ambient temperature, relative humidity and operating voltage during measurement should be recorded. The initial value refers to the measured value at the time of handover test or production test. When the arrester is suspected to be defective, the AC test should be conducted at the same time.

The arrester limits overvoltage, protects insulation of electrical installation, prevents disturbance of normal system state and realizes automatic recovery when the peak value of the overvoltage caused by the lightning or the circuit switch exceeds the rated system value.

Gapless Zinc oxide arresters are connected between the phase and ground terminal to limit the voltage level below the withstand voltage Level of system Electrical equipment. Lightning overvoltage have a time range of few microseconds and the magnitude of the overvoltage can reach several per unit if the lightning arrester is not installed.

Zinc oxide provides nonlinear voltage-current characteristics for the protection from overvoltages. Hence it acts like a nonlinear resistor.

When the syste voltage is applied on the lightning arrester at continuous operating voltage, about 80% of the rated voltage, the arrester eexperience some leakage current which depends on the condition of the arrester. The current consists of capacitive and resistive components. The leakage current generates heat hence proper thermal design is needed for the arrester housing. During lightning surge, Zinc oxide resistance decreases heavily and the current reaches the range of kA. This discharges the voltage surge to the ground.

PCOV: peak value of continuous operating voltage. It should be higher than the maximum operating system voltage.

CCOV: Crest value of the continuous operating voltage. It should be higher than the maximum operating system voltage.

Uref: Reference DC voltage at 1mA current conduction. It is the voltage when the arrester begins to act.

LIPL: Lightning impulse protection Level.  Maximum residual voltage peak value under lightning impulse current.

SIPL: Switching Impulse Protection Level. Maximum residual voltage peak value under operating Impulse current

U500A: Reference DC voltage at 500A current conduction.

U10kA: Reference DC voltage at 10kA current conduction.

Energy: Maximum energy absorption capability.