Contents

A	5

AC Equipment	5

AC Filter	5

AC Station Control	6

AC Yard	6

Auxiliary Equipment and 132kV Power	7

B	8

Back Metering	8

Bipolar DC Transmission	8

Bipole Protection	8

BOT	8

BOOT	8

Bridge Rectifier	9

Bridge Inverter	9

C	10

CAN	10

CCC	10

CET	10

CCME	10

CHINCA	10

Common Cathode Group	10

Common Anode Group	10

Commutation Overlap	10

Converter Transformer	10

Converter Valve	10

Converter Valve Control	11

Converter Valve Protection	11

Current Transformer	11

D	12

Data Logger	12

DC Equipment	12

DC Filter	13

DC Filter Protection	13

DC Line Loss	13

DC Line Protection	13

DC Yard	14

Deionization Tank	14

DFU420	14

E	14

Earth Electrode System	14

EPC	14

ENR	14

Equipment Level	14

F	14

FACTS	14

G	14

GRTS	14

H	14

HVDC	14

HVDC Link	16

HVDC Operation Modes	16

HVDC Control/ DC Station Control	16

Hot Standby Losses	17

I	17

IEC	17

IEC 60044-8 bus	17

Ignition Delay	17

IoT	17

J	17

K	17

L	17

LAN	17

Lahore Converter Station	17

Lightning Arrestor	19

M	19

Main Metering	19

Matiari Converter Station	19

Monopole DC Transmission	20

Mercury Arc Valve	20

MRTB	21

N	21

NBS	21

NBGS	21

O	21

OLT	21

OWS	21

P	21

PCS-9250-EACD DC electronic Current Transformer	21

PCS-9250-EAVD DC electronic Voltage Transformer	22

PPP	23

PMLTC	23

POAC	23

Pole Control	23

Pole Protection	24

Protection Zones	24

PZ61/800Ah-232-200A/220V DC Power Panel	25

Q	25

R	25

Redundancy	25

RPC	25

Redundant Cooling	25

Reverse Osmosis Unit	25

S	25

SGCC	25

Shunt Capacitor	25

Shunt Reactor	26

Smoothing Reactor	26

Station Level	26

SVC	26

System Server	26

T	26

U	26

UHVDC	26

UPS	26

V	27

Valve Hall	27

Voltage Measuring System	28

W	28

X	28

Y	28

Z	28

Zero Flux Current Transformer	28

ZZDFPZ-400400/500– 660/330 Converter Transformer	29

# A

## AC Equipment

## AC Filter

Reactance, Capacitance and Resistance Loss

- There are 16 sub-banks 500kV ACFs and shunt capacitors in total, consisting of 4 banks, with 4 sub-banks each. The bank scheme is 7×SC+3×BP11/BP13+3×HP24/36+3×HP3.

- ACF yard is arranged on the north side of 500kV AC yard.

- Sub banks in each bank are arranged on the same side of the main bus, in a linearly way.

- Equipment inside the fence are connected to the main bus through sub-bank breakers.

- The surge arresters/PTs/earthling switches are arranged under the gantry of main bus.

## AC Station Control

- Sequence Control Function of Converter Transformer switch

- AC Filter Bank Switch Control

- AC Bus/ Branch Control

- Interlocking of AC switchyard (through DFU420)

- AC switchyard analogs (DFU420 measures AC voltages/ currents/ power/ frequency and sends through profibus to AC station control)

- Control and monitoring of auxiliary equipment (pumps)

- Interlocking control of middle circuit breaker

## AC Yard

- AIS equipment are used for 500kV AC yard.

- 500kV circuit breakers are arranged in three rows.

- As to the future phase, 8 complete strings and 2 un-complete strings are configured. 6 complete strings and 4 un-complete strings are built in current phase. Except for the Jamshoro 1 goes out to the north, all the others lines go out to the south.

- 2 groups of converter transformers are connected to AC 500kV strings through overhead lines from north side respectively.

- Four ACF banks are connected to AC 500kV strings through overhead lines from north side respectively.

- 2 sets step-down transformers are directly connected to the 500kV buses through jumper wires respectively. Suspended tubular buses are adopted as 500kV bus. The bus voltage transformers and earthling switches are arranged under the gantry.

- 3/2 circuit breaker connection mode is used for 500kV AC yard.

## Auxiliary Equipment and 132kV Power

- Three power supply lines are provided. One power supply line is connected from the outside and the other two are connected from 35kV station transformers in the station.

- AIS equipment is used.

- The external power supply of converter station is tapping via overhead lines from 132kV transmission line nearby.

# B

## Back Metering

## Bipolar DC Transmission

Metal Conductor is used for sending and receiving circuit.

## Bipole Protection

- Neutral Bus differential

- Station/ Backup Station Ground overcurrent

- NBGS

- GRTS

- MRTB

- Metallic return conductor ground fault

- Metallic return conductor transverse differential

- Metallic return conductor longitudinal differential

- Electrode Line Unbalance

- Electrode Line overload

## BOT

Build Operate Transfer

## BOOT

Build Operate Own Transfer

## Bridge Rectifier

With Commutation overlap and ignition delay

Rectifier Control Modes

- Current Controller

- CIA

- α Control

- Constant DC Current Control

## Bridge Inverter

Inverter Control Modes

- Current Controller

- Constant Extinction Angle (CEA)

- Constant DC Voltage Control Mode

- β Control

# C

## CAN

## CCC

Capacitor Commutated Converter

## CET

China Electric Power Equipment and Technology Co. Ltd.

## CCME

China Chamber of Commerce for Import and Export of Machinery and Electronic Products

## CHINCA

China International Contractor Association

## Common Cathode Group

## Common Anode Group

## Commutation Overlap

𝜇

## Converter Transformer

## Converter Valve

Thyristor, Valve Reactor, DC equalizing resistance, damping capacitance and resistance, steep wave equalizing capacitance, triggering and monitoring equipment. 3 phase short circuit current 36kA.

Valve Status:

- Invalid

- Earthed

- Standby

- Blocked

- Deblocked

## Converter Valve Control

- Sequence Control (Trip, Block, Deblock, Line Fault recovery)

- Converter Transformer Control (Tap changer, cooling)

- Switch Control (Transformer switch, Earthing switch)

- Extinction Angle Forecast

- Firing Angle limit

- Closed Loop Controller (Current, Voltage, Extinction angle)

- Firing Pulse Control (Generation, Ignition)

- Protective Monitoring (AC Voltage Magnitude and Angle, OLT, impulse loss)

## Converter Valve Protection

- Short Circuit

- Commutation Failure

- Overcurrent

- Differential

- Zero Sequence overvoltage

## Current Transformer

# D

## Data Logger

## DC Equipment

## DC Filter

Reactance, Resistance and Capacitance Loss

## DC Filter Protection

- Resistor/ Reactor overload

- Differential

- HV capacitor unbalance

- Detuning

## DC Line Loss

Corona Loss and Insulator Leakage Loss. Pc=U_d1.I_d1+ U_d2.I_d2. Ohmic Loss Id*Id*Rd. 5-7% losses.

## DC Line Protection

- Travelling Wave

- Derivative

- Longitudinal differential

- Undervoltage

## DC Yard

- DC yard equipment are arranged outdoor and symmetric by 2 poles.

- DC pole line equipment are arranged on both sides, DC neutral line equipment are arranged in the center of DC yard, and 2 DC filter banks are arranged between them on each pole.

- Smoothing reactors are arranged separately, 2 for DC pole line and 3 for DC neutral line on each pole.

- The DC pole bus are brought out from the valve halls by bare conductor via post insulators, and the neutral bus is bought out also by bare conductor.

## Deionization Tank

## DFU420

Local Measurement and Control Unit

# E

## Earth Electrode System

## EPC

Engineering Procurement and Construction

## ENR

Engineering News-Record

## Equipment Level

# F

## FACTS

Flexible AC Transmission System

# G

## GRTS

# H

## HVDC

High Voltage DC Transmission

- (Point to Point,

- Low Right of Way/ Transmission Corridor 60% T/L,

- Low Radio Interference,

- Low Losses,

- Large Power Capacity,

- High Tariff,

- No grid connection requirement in middle,

- System stable in frequency and power arc angle oscillations,

- no leakage capacitive currents to ground,

- Limit short circuit current, N

- o need for synchronization,

- Flexible/ Light DC Transmission

- Only two conductors needed.

- Expensive Converter Station,

- Converter Station consumes a lot of Reactive Power,

- Large Filter Devices are needed,

- Converter has little overload capability,

- inefficient DC circuit breakers,

- ground/sea electrodes face corrosion,

- Losses in Converter Transformer, Valves, Smoothing reactors, AC filters etc.

- Equivalent distance of 640-960 km, 5-7% line losses, 1% converter station losses).

High (>3 or >5) Effective short circuit ratio ensures voltage stability during dynamic overvoltages/ instability/ flicker or harmonic resonance)

## HVDC Link

- Monopolar

- Bipolar

- Homopolar

## HVDC Operation Modes

- Pole 1 earth loop mode

- Pole 2 earth loop mode

- Pole 1 metallic return mode

- Pole 2 metallic return mode

- Pole 1 open line test, Pole 2 ground return

- Pole 2 open line test, Pole 1 ground return

- Pole 1 open line test, Pole 2 disconnected

- Pole 2 open line test, Pole 1 disconnected

- Bipolar Current symmetry

- Bipolar Current asymmetry

## HVDC Control/ DC Station Control

- Mode Stabalization (Automatic/ Manual Mode for DC switching. Interstation coordination. Software Interlocking of switchgear ᴧ-AND, Ѵ-OR, A-disconnector open, A-disconnector closed)

- DC Filter Control (Connect/ Isolate, check back supervision, Automatic/ manual driving, mode selection, NB Earthing switch, NB disconnector, DC Line Earthing switch, DC Line disconnector)

- Master/ slave selection

- Bipole DC Power Control (Automatic/ Manual Control, Direction Control, Power ramp rate, Power Modulation POAC (Power order determined through system research, run up and run back, Power Limit, Frequency Limit, Subsynchronous Oscillation Control)

- Auxiliary Reactive Power Control (QPC (Extinction angle change sent to valve bank controller and tap changer), Gamma kick (Temporarily change extinction angle to reduce transient overvoltage when connecting/disconnecting filters))

- Reactive Power Control (RPC) (Limit overvoltages and reactive power exchange with AC system).

- Operation Mode Control (Bipole Power, Monopole Power, Monopole Current Control)

- DC Current Control (Current order/ error PI control balance (Maximum 2% rated current change at rectifier side), margin, coordination, limit, Voltage Dependent Current Order Limit (VDCOL) Control)

- DC Voltage Control (Voltage order, drop, calculation Control, Tap Changer Control)

- Switching Control (Master/ Slave Station and System Level Control, Firing Angle Limits)

- Interfaces (Analogue input (ESP), Binary input/ output (EDI), LAN (to pole control, AC station control, HMI), Fieldbus (to DFU420), IFC (to pole control), TDM, 60044-8 (to station stability device)).

## Hot Standby Losses

No Load Losses

# I

## IEC

International Electrotechnical Commission

## IEC 60044-8 bus

## Ignition Delay

α

## IoT

Internet of Things

# J

# K

# L

## LAN

## Lahore Converter Station

The receiving converter station of the ±660kV HVDC Project from Matiari to Lahore in Pakistan.

1. DC rated power: 4000MW in bipole;

2. DC rated voltage: ±660kV;

3. DC rated current: 3030A;

4. DC outgoing line : 1 line; DC electrode line : 1 line;

5. AC outgoing line : 6 lines;

6. Converter transformer: 12 sets for work, 2 sets for spare, total 14 sets. The capacity of each converter transformer is 400.4MVA;

7. Smoothing reactor: total inductance of each pole is 300mH, 4 sets for each pole, the inductance of one set is 75mH;

8. DC filter: 1 HP6/42 DCF bank + 1 HP12/24 DCF bank for each pole;

9. AC filter: divided into 4 groups and 16 banks, which are 8 HP12/24 ACF banks (150Mvar) + 8 SC banks (160Mvar). 10. 35kV shunt reactor: 4 banks, 60Mvar each;

11. 510/35kV station transformer: 2 sets, 130MVA each;

12. 132/11kV station transformer: 1 set, 10MVA;

13. 35/11kV station transformer: 2 sets, 8MVA each.

Six Bays

- 1st Bay ACF 1 and Pole 1 Converterer Transformer •

- 2nd Bay ACF 2 and Lahore South 1 •

- 3rd Bay Pole 2 Converterer Transformer and Lahore 1 •

- 4th Bay Lahore North 1 and Lahore North 2 •

- 5th Bay ACF 3 and Lahore 2 •

- 6th Bay ACF 4 and Lahore South 2

## Lightning Arrestor

# M

## Main Metering

## Matiari Converter Station

The sending converter station of the ±660kV HVDC Project from Matiari to Lahore in Pakistan.

- DC rated power: 4000MW in bipole;

- DC rated voltage: ±660kV, there are single-12(6*2) pulses wiring, DC rated current: 3030A;

- DC outgoing line : 1 line, DC electrode line : 1 line;

- 4.Converter transformer: 12 sets for working, 2 sets for spare, total 14 sets. The capacity of each converter transformer is 400.4MVA;

- Smoothing reactor: 4 sets for each pole, the inductance of one set is 75mH, and one fore spare;

- DC filter: 1 HP6/42 DCF bank + 1 HP12/24 DCF bank for each pole;

- AC outgoing line : 12 lines for future phase with 7 lots line HV reactors, 10 lines for current phase with 5 lots line HV reactors. One HV bus reactor is configured. The capacity of line HV reactor is 90Mvar per each, and the bus reactor is 180Mvar.

- The long-term targets for Matiari converter station include 12 AC 500 kV outgoing lines, 4 banks of AC filters (hereinafter referred to as "ACF") and 2 converter transformer groups. There are 18 elements in total, which form 8 complete strings and 2 incomplete strings. At present, Matiari converter station include 10 AC 500 kV outgoing lines, 4 banks of ACF and 2 converter transformers. There are 16 elements in total, which form 6 complete strings and 4 incomplete strings. 5 outgoing lines will be equipped with high-voltage reactors. Otherwise， one of the buses will be connected with a HV Reactor.

10 Bays

- 1st Bay ACF 1 and Pole 2 Converterer Transformer •

- 2nd Bay ACF 2 and SECL 1 •

- 3rd Bay Pole 1 Converterer Transformer and SECL 2 •

- 4th Bay TEL Power Plant •

- 5th Bay Port Qasim 1 and THAL NOVA Power Plant •

- 6th Bay ACF 3 and Port Qasim 2 •

- 7th Bay ACF 4 and Spare 1 •

- 8th Bay Jamshoro 1 and Spare 2 •

- 9th Bay Jamshoro 2 •

- 10th Bay Moro and Dadu New

## Monopole DC Transmission

Transmission Line has only one metal conductor. Ground or sea water is used as the return circuit.

## Mercury Arc Valve

High Fault Rate of Reverse Arc, Low Reliability

## MRTB

# N

## NBS

## NBGS

# O

## OLT

Manual/ Automatic Open Line Test to test insulation capacity of main equipment

## OWS

Operator Work Station

# P

## Panels

| HCM3000 Device | EPU20B Panel |  |
| --- | --- | --- |
|  | SR10D Rack |  |
|  | ENT10B Panel |  |
|  | ESM10B Panel |  |
|  | ITM10C Panel |  |
|  | IFC20A Panel |  |
|  | EFM20A Panel |  |
|  | EVI11A Panel |  |
|  | EVC10A Panel |  |
|  | EDI10B Panel |  |
|  | ECM10A Panel |  |
|  | EOT11C Panel |  |
|  | ESP10C Panel |  |
|  | ETS11 Panel |  |
|  | BEM10 Panel |  |
| DFV100 Device | TCU10 |  |
|  | TVI10 |  |
|  | DDI10 |  |
|  | DDO10 |  |
| HPL100 Device | XS931/3A |  |
|  | EPLM20 |  |
|  | EPLI10 |  |
|  | EPLR10 |  |
| DFU410A Device | TAC10 |  |
|  | TAB10 |  |
|  | TVC10A |  |
|  | TVM10A |  |
|  | TVB10B |  |
|  | TCN11A |  |
| DFU420 Device |  |  |
| DFM411 Device | XAIM11 |  |
|  | XDIM10 |  |
|  | XDPM11 |  |
|  | XPSU10 |  |
|  | XOIM10 |  |
|  | XOTM10 |  |
|  | XPFM11 |  |

## PCS-9250-EACD DC electronic Current Transformer

3030.3 A

- (1)Primary sensor: Low-Power CT (LPCT) is used to transduce AC current.

- (2) Resistor box: it functions as signal distribution, converts one analog signal to multiple signal outputs. It is equivalent to a high power, high temperature resistance, low temperature coefficient, precise, and low value resistor. The rated output of the shunt is about 75mv, for 3030.3A rated primary current, the shunt resistance is designed to be 25uΩ. The shunt is made of Manganese-Copper alloy, and  it is designed as “symmetric squirrel-cage structure” to realize good heat dissipation and anti-interference.

- (3) Remote terminal unit: also called primary converter, it is located at high-voltage side and used for data acquisition, multiple RTUs can be configured in ECT. Receiving the analog signal output from the resistance box, after filtering, sampling, electro-optical conversion, etc., it gives an output of serial digital optical signal. Located at high voltage side, its power supply is provided by the merging unit through the laser light. An optical fiber receiving connector(FC type) is used to receive laser, and an optical fiber transmitting connector(ST type) is used to send digital signals. low-power design and dual sampling.

- (4) Optical fiber insulator: it is a solid composite insulator with embedded optical fibers. When installed in suspension type, using suspended optical fiber insulator. And also could be support type. The insulator is embedded with 24 or 32 multi-mode optical fibers, and the spared optical fiber core is not less than 100%. The insulation structure is simple and reliable, mainly bearing its own weight and wind load for suspension type.

- (5) Merging unit: placed in the control room. It is used for providing laser energy to power RTUs, receiving  and processing  the data from the RTUs and transmitting  them to the  control & protection system according to IEC 60044-8 protocol. Self-monitoring function, monitoring parameters: laser driving current, receiving data level, RTU temperature, laser temperature, parity check error times.

## PCS-9250-EAVD DC electronic Voltage Transformer

660kV

- (1)DC voltage divider:  it  adopts resistor voltage divider  with capacitor  compensation, the resistors and capacitors are located in a silicone rubber composite-insulation cylinder, and the inside is filled with SF6 gas.

- (2) PCS-9559 IO unit: it is used for analog quantity isolation, installed in cabinet at the control room. The device is connected with the DC voltage divider through four-core double-layer shielded cable. Each DC voltage divider is equipped with three sets of PCS-9559 IO unit. The rated output signal of PCS-9559 is 5V  The main function of PCS-9559 IO unit is to divide and isolate the output signal of DC voltage divider. Each PCS-9559 is equipped with one resistor voltage divider (NR1478) and two isolation output modules (NR1411). Each DC voltage divider must be equipped with three sets of PCS-9559 IO units. The rated secondary output of the device is ±5V.

## PPP

Private Participation in Infrastructure Projects

## PMLTC

Pak Matiari-Lahore Transmission Company Pvt. Ltd. responsible for 886 km, +/- 660 kV, 3030 A, 4 GW, 1971 Self-Supported, Double-Circuit Towers, 388 (242+146) Electrode Line Towers, Quad-bundle 4*1250 mm2 conductors (Matiari-Sukkur 214km ACAAR 4*JL1/LH1-800/550) + (Sukkur-Lahore 664km ACSR 4*JL1/G3A-1250/70), 24 Fiber OPGW-120 * 2 Shield Earth Wires, Substations (TEL 330MW, ENGRO THAR 2X330MW, THAL NOVA 330MW, SECL/TCB-1 660MW (+660MW), SIDDIQUE SONS 330MW, PORT QASIM 2X660MW, LUCKY ELCTRIC 660MW. K2 NUCLEAR POWER 1100MW, JAMSHORO, DADU NEW, MORO) HVDC Transmission Project (1 Dec 2018-2043 Commercial Operation Date 1 Mar 2021).

## POAC

Power Order Calculator

## Pole Control

- Master/ slave selection

- Sequence Control (Start, Stop, OLT)

- DC Line Fault Recovery

- Power Control

- Power Direction Control

- Power Modulation (run up and run back, Frequency Limit, Subsynchronous Oscillation Control)

- Converter Status Control (Current, Voltage, Angle)

- Tap Changer Control (Position/ running/ faulty signal, control (No load, Angle, Ud, gamma controls))

- Operation Mode Control (Bipole Power, Monopole Power, Monopole Current Control)

- DC Current Control (Manual/ Auomatic Control, Current order (single pole mode, bipole mode, pole synchronous mode, communication failure mode), current balance, current margin compensation (maintain pole current order), coordination, limit (based on equipment overload (2s, 2h, continuous)/ filters/ power limit/ protection request/ blocking/ deblocking/ VDCOL), VDCOL Control)

- DC Voltage Control (Voltage order, drop, calculation Control during different modes and fault recovery)

- Extinction Angle Control

- Firing Angle Control

- Selection of Controller

- Auxiliary Reactive Power Control (QPC, Gamma kick)

- Switch Control and Monitoring

- Protective Monitoring (X/ Y/ Z block (Force retard, Block firing pulses, Trigger bypass, Trip circuit breaker), large angle monitoring, fast shut down, AC voltage limit)

- Commutation Failure Protection (zero sequence voltage criterion, constant extinction area criterion)

## Pole Protection

- DC overvoltage

- DC undervoltage

- 50 Hz/ 100 Hz

- Pole busbar differential

- Neutral busbar differential

- Pole differential

- Electrode Line Open

- Ac/ DC Line touch

- NBS

- Neutral bus capacitor protection

## Protection Zones

- Converter

- DC pole bus

- DC neutral bus

- Line

- Bipole (NBS, NBGS, GRTS, MRTB)

- DC Filter

## PZ61/800Ah-232-200A/220V DC Power Panel

AC Distribution Unit, HF rectifier Module, insulation test module, DC Feeder unit, centralized monitoring module.

# Q

# R

## Redundancy

2 out of 3 principle

## MiCOM Relays

## RPC

Reactive Power Control

- Overvoltage Control

- AbsMinFilter

- U_Maximum/ U_Minimum

- Q_Maximum

- MinFilter

- Q_Control/ U_Control

## Redundant Cooling

## Reverse Osmosis Unit

# S

## SGCC

State Grid Corporation of China

## Shunt Capacitor

Harmonic Loss and power frequency loss

## Shunt Reactor

## Smoothing Reactor

DC loss and harmonic loss

## Station Level

## SVC

Static VAR Compensator

## System Server

# T

# U

## UHVDC

Ultra High Voltage DC

## UPS

Normal Mode

Static Bypass Mode

Backup Mode

Maintenance Bypass Mode

# V

## Valve Hall

- Twelve converter transformers are arranged in a linear way in the west of the valve halls, and every six sets corresponds to the one pole.

- The bushings of converter transformer on valve side are inserted into the valve hall and connected to valves after Y/Δ being connected. Converter transformers are separated by firewalls.

- The towers of junction bus are located on the north and south sides of the fire walls, making the junction bus above the converter transformers.

- The incoming line of converter transformers is brought from 500kV AC switchyard.

- The junction bus is hanged in a higher position whereas the incoming line crossover beneath it.

- The surge arresters of valve-side of converter transformer, the RI capacitors, the surge arresters, the CTs of the neutral point, and the post insulators are all located on the top of the fire walls.

## Voltage Measuring System

# W

# X

# Y

# Z

## Zero Flux Current Transformer

## ZZDFPZ-400400/500– 660/330 Converter Transformer

Insulation Level

Transformer Oil

Maintenance