## Slide 1
Chapter 2 (part I)

## Slide 2
Introduction
Control and protection equipment is layered and distributed in three levels
Operator level
Control and protection equipment level
Field measurement and control equipment level
All the levels and control equipments are connected with each other through network busses and other interfaces, converter stations are connected through dual intercommunication channels to form a complete DC station control and protection system.
Pole control is at control level, exchange data with the operator through LAN, issue orders and display status through OWS.
Measurement board is used to collect and process the analog required by system, AC analog is obtained from hard wiring and DC is obtained partially from hard wiring and partially by optical fibres
Important data is transferred between pole control system and other systems like VCE at control level through hard wiring and optical fibres.

## Slide 3: Important abbreviations:
Abbreviation | Detail
QPC | Converter Reactive Power control
TCC | Tap Changer Control
RVC | Rectifier Voltage Calculator
DVC | DC Voltage Control
CBC | Current Balance Control
SER | Sequence of Event recording
TFR | Transient Fault Recording
VCE | Valve Control Electronics
ESOF | Emergency Shutdown
Imin | Minimum Dc Current
α | Firing Angle
γ | Extinction Angle
UD | DC Voltage
DC | Direct Current

## Slide 4: Functional scope
The DC Control system of the project can be divided into 3 levels:
1- Bi-pole level 2- Pole level 3- Converter level
Basic Functions:-
Communication function
The basic function includes communication function and the types of communication function can be defined as:
LAN communication
Field communication
Control bus communication
Fast interstation communication
Modulated wave optical fiber communication

## Slide 5
IEC60044-8 bus communication
GOOSE bus communication
TDM bus communication
Hardware Monitoring
Software Monitoring
Redundancy Function
System selection control
Signal switching logic
Redundant real-time tracking

## Slide 6: 1-Function of Bi-pole Level
The functions of the Bi-pole Level are implemented in the DC Station Control host to provide pole DC power orders to the pole control hosts of both poles.
DC power orders are distributed to the pole control hosts of each pole according to the Bi-pole DC power orders issued by the HMI system, additional control, current balance control of double poles, emergency pole-pole power transfer and other factors.
The DC station control host is also responsible for relevant sequence controls, Reactive power control and AC bus voltage control of the whole system.

## Slide 7: 2-Function of pole level
This is implemented in pole control host
It calculates dc current and dc voltage reference according to the monopolar DC current/ monopolar DC power order from HMI ,thus converter level control is close loop
Pole control host of one station also communicates with pole control host of other station

## Slide 8: 3-Function of Converter Level
Converter level with its functions realized by the pole control host is mainly used for following:
Closed Loop Control of DC Current Controllers.
Closed Loop Control of DC Voltage Controllers.
Closed Loop Control of Extinction Angle controllers.
It does all of the above according to reference value of DC current and Voltage.
This layer also converts firing angle instructions into firing pulses, Enabling/disabling sequence control, steady/transient operation control and emergency enabling/disabling sequence control in case of fault.

## Slide 9: Pole control system and its cabinet
Each converter station (Matiari or Lahore) has 2 poles
Each pole is equipped with 2 redundant pole control systems (A and B) and each system is installed in its own cabinet
So there will be total 4 cabinets in each station
So in total 8 cabinets including Matiari and Lahore stations

## Slide 10: Concept of Pole Control
The pole control system ensures the normal operation of DC transmission system.
It is used to stabilize DC voltage and current by regulating firing angle at the rectifier and inverter station and tap changer of the converter transformer as required by operator or current operating conditions
In addition, it also has control of de-block/block sequence of converter valve, ensures smooth start/stop of the system and improve the additional controls of the whole system

## Slide 11
Thank you