## Slide 1: 1.4.4. Selection and Switching of Control Position
The switching of control position of each functional group:
System Level
Station Level
is completed separately in DC station control with position status sent to pole control system.
Request-release logic
The master control position is selected by request-release logic. Switching is executed only if a request is received from other control positions. Master control position must be released within 60sec, otherwise the request is considered invalid.
If the request is for a remote dispatching center control position, the control position can be switched directly without release so that operators can take over control any time.
In case of DC station control system LAN communication fault and communication fault between workstations at effective control positions, control positions are set to an undefined status, SER alarm of respective functional group is generated and the control can be handed over directly without release if there is a request.

## Slide 2: 1.4.5. Selection and switching of Control Level
The system control level can be switched in the master control system of any station provided that:
DC Station Control Communication is normal: LAN connected to DC Station Control of other station and LAN connected to an effective system control position.
Pole 1/2 Control Communication is normal: IFC communication connected to DC Station Control and LAN connected to an effective system control position.
The DC station control receives switching orders from other station. The actual control level is sent to the pole control system for switching of settings and to the HMI system for display.
Master/ Slave stations are allocated by station control software through request/ release logic. The slave station can request to act as master station at any time, but the master must release control within 1 minute of the request for the successful transfer of master station functions.