## Slide 1: PMLTC Converter Transformer Protection

## Slide 2: Converter Transformer
The converter transformers step up the voltage of the AC supply network. Using a star-to-delta or "wye-delta" connection of the transformer windings, the converter can operate with 12 pulses for each cycle in the AC supply, which eliminates numerous harmonic current components.
TYPES:
The converter transformer is available in four designs, namely
Three-phase three-winding
Three-phase two-winding
Single-phase three-winding
Single-phase two-winding

## Slide 3: Main Abbreviations
Abbreviation | Detailed description
AC | Alternating Current
DC | Direct Current
BF | Circuit Breaker Failure
CB | Circuit Breaker
TA | Current Transformer
TV | Voltage Transformer
SER | Sequence of events recorder
TFR | Transient Fault Record
MMI | Man Machine Interface
HMI | Operator Control System

## Slide 4: Functional Scope
Protection Scope:
The zone of converter transformer compromises conductor and all equipment from the AC Circuit breaker connected to the Grid side to the wall bushing on the valve side.
Protection Function:
Protection of Converter Transformer is threefold to ensure that the protected area is protected correctly, just in case if any single component failure occurs, it must not cause the wrong operation of the protection system. Hence, the reliability increases.
Double device with the logic of (2 out of 3) are installed in the Converter Protection Panel A and B. There is no (2 out of 3) logic device on the panel C. When all the threefold converter transformer protection system working properly, at least two of the similar protection system will start tripping, a signal will be sent to Control system through optical fibre to clear fault.
In case of an Internal Fault the “Two out of three” logic will be switched automatically to single redundant protection configuration.

## Slide 5: Functional Scope
Each protection is totally independent physically and electrically, has its own independent power supply. In case any protection is quitted due to failure, maintenance or other reason. The other protection is not effected and the Whole HVDC systems runs normally. Hence this makes our system more accurate and sensitive.
PAC-886 is the main as well as backup protection that will operate if the Logic “2 out of 3” Operates. This device is used in Converter station to meet the requirements of GOOSE tripping and analog sampling.
Protection Configuration:
PAC-886 provides protection of all electrical quantities required by each valve group converter transformer.
1. Main Protection:
Transformer Overall Differential Protection (87TC)
Connection Differential Protection (87C)
Transformer Differential Protection Y/Y (Y/Y 87 CN)
Zero Sequence Transformer Differential Protection of Y/Y (Y/Y 87CN)

## Slide 6: Functional Scope
Protection Configuration:
2. Backup Protection:
Connection Overcurrent Protection (51)
Over Voltage Protection (59T)
Over-excited Protection (24T)
Y/Y net overload Protection (Y/Y 49)
Connection Differential Protection (87C)
Scope and Purpose of Protection:
Covers the protection between the CT at connection and CT at original side of Converter Transformer.
Principles and strategies of protection:
The protection will operate if the differential current is greater than the setting.

## Slide 7
Protection coordinate:
Setting should be selected in such a way that the connection of converter can be protected.
Logic and setting principle of setting
Instantaneous Differential Protection:
Idiff = 5 * IN, Trip Immediately (typically 5ms)
where, IN is the rated current flowing in the original side of the converter.
Biased Differential Protection:
Immediate trip delay with restrictive conditions: Typical time 15ms.
Protective action sequence:
  Trip AC circuit breaker
  Lock Ac Circuit Breaker
Backup protection:
  Connection and Transformer Differential Protection
  Connection Over-Current Protection

## Slide 8
1:Connection differential protection:(87C)
Purpose:
The protection zone is between the CT at connection and the CT on the original side of the converter transformer.
To detect the ground fault on connection.
Backup protection:
Connection and transformer differential protection.
Connection over current protection.
2:Connection over current protection:(51)
Purpose:
To protect and measure the over current on the converter connection.

## Slide 9
Backup protection:
Converter transformer body protection (e.g: oil, pressure relay).
Converter transformer zero sequence over current protection.
3:Connection and transformer differential protection:(87TC)
Purpose:
Use to detect the failure of both connection and converter transformer.
Backup protection:
Connection over current protection.
Buchholz relay protection.
4:Transformer differential protection:(87T)
Purpose:
Use to detect the grounding and inter turn short circuit faults between the CTs on the converter transformer net and valve side.

## Slide 10
Backup protection:
Connection and transformer differential protection.
Connection over current protection.
Zero sequence over current protection.
Converter transformer body protection.
5:Transformer over current protection:(50T)
Purpose:
To detect short circuit faults in converter transformer.
Backup protection:
Connection over current protection.
Zero sequence over current protection.
Converter transformer body protection.

## Slide 11
6:Connection over voltage protection:(59T)
Purpose:
To avoid serious continuous AC over voltage which will damage the converter transformer and bridges.
Backup:
Backup protection for other protection.
7:Transformer overload protection:(49)
Purpose:
To test the net side overload capacity of converter transformer.
8:winding transformer differential protection:(87TW)
Purpose:
To detect the grounding fault of the converter transformer winding to prevent winding damage.

## Slide 12
Backup:
Connection and transformer differential protection.
Zero sequence over current protection.
DC differential protection.
9:zero sequence over current protection(50TN):
Purpose:
Used for Y winding of converter transformer to detect single phase or phase to phase short circuit fault and protect transformer.
Backup:
Backup for transformer differential protection.
10:Over excitation protection:(24T)
Purpose:
Detect over excitation of converter transformer.
Backup:
Voltage stress protection.

## Slide 13
Zero Sequence Differential Protection(87CN)
It detects internal ground fault and winding fault of the original side winding of converter transformer.
It compares zero sequence current of three phases of original winding at both end and if it exceeds ref. value then protection will be act.
Its coordination is with converter differential protection.
Its sequence of protection will be:
Exit of corresponding 12 pulse converter
Trip of corresponding AC breaker
Lock the corresponding A.C Circuit Breaker
Start the corresponding C.B failure protection
Zero-sequence Over-Current protection acts as backup protection here.

## Slide 14
DC saturation protection
It protects converter transformer from DC saturation because of DC current entering through its neutral.
Whenever transformer operates unbalance DC current enters its neutral that current is monitored. This DC current will distort the excitation current of transformer.
Choice of setting is determined by DC current/magnetization peak that transformer can withstand continuously. And protection is in two stages: Alarming and Tripping.
Y/Y transformer is equipped with this protection but Y/D is not equipped with this protection.
Its sequence of protection will be:
Alarm
Exit of corresponding 12 pulse converter
Trip of corresponding A.C circuit breaker
Start the corresponding C.B failure protection
Lock the corresponding A.C circuit breaker
DC harmonic protection acts as backup protection here.

## Slide 15
“Two out of three” Tripping Logic
The processing mode for three sets of completely independent protection for electrical quantity is:
If any one group results 1 and other two 0 then protection will not act.
If any two groups are defined as 1 or all three results 1 the will act.
“One out of two” Tripping Logic
In case of “two out of three logic failure” the processing mode of GOOSE is:
If all three groups results 0, the protection will not act.
If any one is defined as 1, protection will act.

## Slide 16: Hardware Description
CONFIGURATION:
There are 24 protection panels in Matiari and Lahore converter station
Each station has 12 panel
12 panels are divided as 6 electrical panels and 6 non electrical panels
There are 3 electrical protection system of which A and B are similar and independent also
System C has no “Two-out-of-Three” circuit and external signal output circuit
Hardware system:
8MF panel is used in Matiari-Lahore ±660KV DC Transmission Project which has high strength of structutral parts and good sealing.

## Slide 17
Working Power Supply:
Each Chassis is equipped with dual-channel power supply to ensure normal operation even if any one power supply fails.
Each converter transformer protection system is supplied by two DC220V circle. If the load in the panel is overloaded or the power supply is short-circuited, the air switch will automatically cut off the power supply. And Red light on the panel Lights up and alarm information is uploaded to SER Panel.
The power supply of lighting system in the panel is AC220V.
Software:
All protection software is implemented on the unified software platform using VLD visual logic programming tools. The protection source code is completely automatically generated by the software robot and the accuracy rate is 100%.

## Slide 18
Interface and Signal of Protection System:
Interface with primary measuring equipment: It is on the local terminal box of the measuring device and includes 3 phase current and voltage on valve side of converter transformer, 3 phase current on grid side, neutral current on valve side and busbar voltage and current of incoming.
Interface with synchronous clock source: It is on the main clock system cabinet
Interface with AC protection: The output signal is used to start the CB failure protection. It is on the converter transformer protection cabinet. Dry contact, 220V, 5A
Interface with transient fault recorder system: The output signal includes Protection actions and instructions for self-monitoring faults to start the transient fault recorder system. It is on the converter transformer protection cabinet. Dry contact, 220V, 5A

## Slide 19
Panel Layout:
The front panel has 7 signal lights with 2 lights for standby.
RUN (Running) (Green)
Abn (Abnormal) (Red)
Overhaul (Overhaul) (Red)
87.Pro.Blk. (Differential protection lock) (Red)
Pro.Trip. (Protection tripping) (Red)
Action and Exception handling:
If an abnormality in CT or PT is reported, the corresponding protection is blocked.
The overload warning means that the load current exceeds the alarm setting and we have to transfer the load
Differential current out of limit action means that differential current value exceeds the limit setting and for handling this CT secondary circuit and setting is checked.

## Slide 20: Cabinet Appearance & Fiber Inspection
All equipment sign, signal lights should be correct and connecting pieces ,cable numbers indicate correctly with drawing.
The plugs connection should be tight and corrosion free. Circuit should be dust free environment parameters like temperature, humidity exist in their desire limit.
Device panel is flexible in Operation and panel is grounded too.
Fiber optic connection are in correct and reliable position.
Check the abnormal sound and vibration.
Use vacuum cleaner to clean .Print the control system fixed value setting. The values shoud be in described limits.

## Slide 21: Optical Fiber Visual Inspection
Check bending radius fiber.it should be not less than 15 times the outer diameter of the fiber.
Use optical power meter to measure each fiber in the screen.
Select the specified wavelength on the optical power meter turn on the light source ,the optical power meter display value is the attenuation value of the fiber under test .
Electric-Optic Conversion module inspection, The model quantity and installation location of the device should be consistent with the design drawings.

## Slide 22: Secondary circuit and anti-interference check
The Secondary wired of AC and DC should not share the cable.
The cable heads of all the outdoor cables such as CB,CT,PT should place in the Junction box. when the cable adopts multi-strand flexible wire .it must be connected to the terminal through crimping terminal.
Trip circuit insulation check before inspection it must be confirmed that CB is powers off before it is allowed to proceed.
Disconnect the external wiring of the measure trip terminal at the control panel

## Slide 23: DC current check
DC air switch and DC fuse configured in the screen shall have name plate with equipment.
The fuse should not be connected to the next level of the DC air switch .
Put all AC and DC power supply air switches in the control system
Use 1000 v megohmmeter to measure thte insulation resistance of the device and resistance value is greater than 1Mohm .
Insulation check (3 years):
Check the resistance of the devices by using 1000V mega ohmmeter. Resistance should be more than 1MΩ.

## Slide 24
DC conversion power check (3 Years):
All plug-ins should meet the requirement. The device running lights should work normally and device operates normally.
GPS/ Beiduo time(3 years):
You can observe the monitoring background alarm by opening the timings terminal to detect whether the timing node is intact.
Control system switching test (3 Years):
Check the switching between system A and B and observe the running indicator on panel whether displayed correctly or not.
Terminal inspection and tightening (3 Years):
Tight the terminals of DC control system of the entire station so that no terminal left loose.
Control protection software check (3 Years):
Check whether the control program is latest version, whether the application is upgrade, version number and other records.

## Slide 25
Control protection software check (3 Years):
LAN network communication check (3 Years):
Specify the address of the LAN communication software.
Fieldbus communication check (3 Years):
Clear the address of the fieldbus communication software.
Device power supply circuit inspection (3 Years):
Check if there is another independent power supply after the device loses power to ensure that the system can operate normally.

## Slide 26: Non Electric Quantity System of converter Transformer
The non-electric quantities of converter Transformer like Oil Temperature, Pressure , humidity level is very important and they need to be carefully monitored and if these values go beyond their preset level a protection must operate to avoid any further damages. For monitoring we have non electric quantity acquisition system of converter transformer.
Functional Scope:-
Protection scope
The protection device provides the collection of all non-electric quantities required by converter transformer.
Protection function
In order to insure the reliability of converter Transformer , the triple scheme is adopted to ensure its reliability to avoid mis operation. The triple scheme is basically to choose 2 out of 3 input to decide the output operation.
Function Describes:-
Status acquisition
For the monitoring the continuous status of converter Transformer the device PAC-837 is used which has 105 photoelectric isolated idle contact DIs (Digital Inputs).
The digital input information is sent through GOOSE (Generic Object Oriented substation Events)

## Slide 27
Maintenance Function
The device is provided with a “maintenance status” link. When the maintenance link is enabled the panel indicator indicates that the device is in a maintenance mode. In this Case , the device sends GOOSE (Generic Object Oriented substation Events) message with corresponding maintenance position setting in the message
Time Synchronization
The time synchronization is very important and this device has a synchronization interface with external standard time service source. The accuracy of synchronization is ≤ 1ms.
Self Check and Alarm Function
The device PAC-837 has a self check function covering self check items such as Program, Power Voltage(5V/24V) and serial port interruption. The status of ‘device alarm “ is generated in any one of the device self check error.

## Slide 28: Hardware Structure:-
Overall Configuration
There are 6 non electric quantity panels in Matiari and Lahore Converter Station. The overall technology used improve the reliability of device hardware.
Hardware System
We have adopted 8 MF Panel in this project which has the advantages of high strength of structural parts, good sealing, and good adoptability to various complex environment.
Working power
Each cabinet is equipped with independent two-way Power supply at he same time to ensure the normal operation of the device in case of loss of any Power supply. If any Power module fails, it will output the alarm contact and send the message to monitoring system.

## Slide 29
Software Description:-
All the protection software is completed by independent development.in order to ensure the correctness of the protection function and reliability of system operation. The development process has experienced repeated and strict processes.
Interface and signal of converter Transformer non-electric system:-
The interface between the non-electric power system and the local control cabinet adopts the mode of idle contact. The signal includes the signal collected by the local control cabinet of converter transformer.
Interface with Pole Control
Connect to Pole control with GOOSE (Generic Object Oriented substation Events)
Interface with synchronous clock source
The interface signal between converter transformer non electric system and synchronous clock source is IRIG-B. The interface is on the main clock system panel

## Slide 30: PAC-837 Front Panel Layout
Seven signal lights
Running: Green (normal operation), off (no power or self check error)
Alarm: Red (Device Alarm detected), off (normal operation)
Maintenance: Red (Maintenance enabled), off (normal operation)
Time Synchronization Abnormal: Red (Time Synchronization Abnormal), off(normal operation)
Action of DI/ DO: Red (Dithering/ noise Elimination performed for any of 102 Digital Inputs: 7# board has 1-18 DIs, 8/9/C/D# boards have 1-21 DIs each), off (normal operation)
Standby: Spare
Standby: Spare

## Slide 31: PAC-837 Maintenance items, cycle and requirements of action
DC Operation and Protection System Operation and Maintenance rules:
Cabinet Appearance Inspection: Every year check screen cabinet, wiring, signs, signal lights, connections, plugs, buttons, fiber optic terminal box and spare fiber reels
Setting Check: Every year, print control system fixed value order and compare each value with reference fixed value sheet for approval.
Fiber Optic Loop Inspection: Every three years, check fiber optic terminal box, multi-strand wire crimping terminals and connectors.
Electro-optic Conversion Module Inspection: Every three years, check wiring connections and compare with design drawings. The wires must not cross.
Secondary Circuit and anti-interference check: Every three years, check the cable heads/ numbers/ labels/ Insulation/ models/ connections.

## Slide 32: Maintenance Items
Trip Circuit Relay Verification: 06 Years, Operate 55%-70% of the rated voltage.
Anti-interference Grounding Check: 03 Years, Cross-sectional of screen should not be less than 100mm2. Lower part of the cabinet should be equipped with copper bar (Grounding cable 500mm2). Panel shelf should be grounded.
DC Current Check:
  DC Air Switch and Fuse check: 03 Years, Not used AC air switch instead of DC, should have name plate with name and No. DC air switch and fuse must be match with other.
  Parasitic loop inspection: Measure AC and DC voltages on load side after pulling all AC, DC power supplies in air switches and confirms there is no parasitic loop.
Insulation Check: 03 Years, Use 1000V M Ω meter for resistance measurement value should greater than 1MΩ.

## Slide 33
DC Conversion Power Check: 03 Years, Check all plug are plugged in , Turn Off and On, Check running lights.
Input / Output Check:
  Binary Output: Check all inputs on terminal box. Use Short and open circuit test to test the circuit.
  Output: Check circuit by looping and by software with drawings.
GPS/Beidou time: Monitoring Alarm by opening time terminal.
Control System Switching: Check system A and B and indicators on panel, work normally.
Whole Group Transmission Test: Check logic of trip switch and loop wiring test. Start fault recorder and send information to DC control system to observe AC inlet switch tripped. Check CB trip normally.

## Slide 34
Terminal Inspection and Tightening: Ensure the terminal of DC Control system are not loose.
Control Protection Software Check: 1 Year, make sure the software is upgraded and latest version and its backup is available.
LAN network communication check: Specify address of LAN communication S/W. In engineer’s workstation find the S/W address for communication checking.
Device Power Supply circuit inspection: Check another power supply so that system may run normally after device power loose.

## Slide 35: Thank You