Valve Control Electronics (VCE) Panels

Muhammad Shamaas

VCE800

A VCE800 set corresponds to each 12-pulse valve group. It includes 6 control cabinets, which respectively correspond to A/B/C phase of YY Transformer and A/B/C phase of YD Transformer. The VCE monitors the function of Thyristor, Converter locking, power supply monitoring, control signal monitoring, fault recording, Converter valve tower water leakage detection and control/ monitoring of valve arrester.

FCK 213

Valve measurement and control device for one valve containing 100 Thyristors.

Interface plugin J1/J2: Receive control signals (REC_TRIG, ENERGIZED, DBLK, BYPASS, INV_IND, ACTIVE, SYS_PASS) forwarded from FCK 221. Send FP signal to pole control. Send TRIP signal and VCE_RDY to FCK221. Provide 24V power input interface for this device.

MC Processor plugin D1/D2: Receive FCS from pole control. Control LE and LR plugin to send Trigger pulse. Handle TRIP and VCE_RDY logic. Message processing. Fault recording.  Receive timing signal and OLT_MODE.

LE Light emitting plugin B2-B5: Send Trigger pulse and optical channel detection pulse to 7 components of valve.

Light receiving plugin B8-B9, B11-B13, B15-B16: Receive back inspection signals of Thyristors and optical channels.

Indicators

System A and System B

- RUN: The green indicator light is always on indicating that the power module of the system works normally

- ACT: the yellow indicator light is always on, indicating that the system is the main system. Under normal circumstances, only one indicator light of the system is on.

- PRC: The yellow indicator light is always on, indicating that the system is in the pre-inspection Operation mode. Under normal circumstances, only one indicator light of the system is on.

- DBLK: The yellow indicator light is always on, indicating that the system is in communication mode. Under normal circumstances, only one indicator light of the system is on.

- PCF: The red indicator light is always on, indicating that the system is abnormal in self Inspection and there is plugin fault.  Please inquire OWS for specific alarm information.

- COF: The red indicator light is always on, indicating that the communication between the system and the valve control interface device is abnormal.

- ALARM: The red indicator light is always on, indicating that there is alarm in the system. Please inquire OWS for specific alarm information.

- TRIP: The red indicator light is always on, indicating that the system has a fault. Please inquire OWS for specific alarm information.

FCK221

Valve Control Interface Cabinet.

POWER plugin P1: provide power input for cabinet output power to each plugin.

DIO plate DI and DO plugin J1: Monitor DC power supply, fan power supply, laser emission power supply and device temperature.

CPU board Processor plugin B1: Core function calculation, fault judgement,  device communication, message output, receiving control signals.

TX board B2-B5: HDLC communication between cabinets.

OPTDI board B8-B9: Receive VCE_TRIP and VCE_RDY of FCK 213 and send to controller.

OPTDO board B10-B17 Receive control signals from pole control and forward to FCK 213 and FCK215.

Indicators

- POWER: The green light is always on indicating that the power Module of the system

- TEST: The green light is always on indicating that the system has entered the

- VOLTAGE: The green indicator light is always on indicating that the charging signal sent by the

- DBLK: The green indicator light is always on indicating that the unlocking signal sent by the

- ACT: The green indicator light is always on indicating that the active signal sent by the

- BPPO: The green indicator light is always on indicating that the bypass signal sent by the

- INV: The green indicator light is always on indicating that the system is effective (1MHz) in

- SPARE: Standby

- VCE_RDY: The red indicator light is always on indicating that the VCE_RDY signal from valve

- TRIP: The red indicator light is always on indicating that the trip signal from valve control to

- COM: The flashing yellow indicator indicates that PROFIbus communication between valve

- GPS: The flashing yellow indicator indicates that the GPS timing signal is normal.

- A1: The flashing yellow indicator indicates that the communication between the system.

- A2

- A3

- A4

- A5

- A6

- A7

- SPARE: Standby

FCK215

IO (J1/J2) Interface plugin: provide cabinet power supply, alarm signal output and indicator control.

MC (D1/ D2) Master control plugin: system communication, water leakage and lightning arrester state processing.

LE(B3,B4) Light emitting plugin: Output pulse for primary and secondary water leakage detection of 6 valve towers.

LR_vwl (B7-B8) Light receiving plugin: receive pulse for primary and secondary water leakage detection of 6 valve towers.

LR_surge B11 Light receiving plugin: Monitor the action of 12 way valve arrester.

Indicators

System A and B

- RUN: The green indicator light is always on, indicating that the power Module of the system works normally.

- ACT: The yellow indicator light is always on, indicating that the system is the main system. Under normal circumstances, only one indicator light of the system is on.

- SPARE

- SPARE

- PCF:

- COF

- ALARM: The red indicator light is always on indicating that there is alarm in the system. Please inquire OWS for specific alarm information.

- TRIP