## Intro
Monopolar Low Power Tests Dispatch Matrices
A | All these tests will be performed in Monopolar Mode.
B | Sequence as mentioned in sequence table shall be followed
C | Test Block LP1 & LP2 must be carried out first to verify that control systems of both poles are fully functional. No any other test should be conducted if LP1 & LP2 were unsuccessfull.
D | General conditions and System configurations must be selected as indicated before performing each test.
E | There are four voltage reactors available at Matiari and two LV reactors available at Lahore converter station.
F | AC system short circuit level has been measured prior to commissioning test each day, at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
G | Furthermore, prior to the commissioning test each day, the following tests shall be performed without energization at both stations:
（1） Inter-station telecommunication check of control and protection signals
（2） Dry run connect/isolate pole
（3） Repeat as above with system change over during sequence
（4） Dry run metallic/ground return transfer
（5） Repeat as above with system change over during sequence
（6） Emergency stop, dry run.

## Sequence
Matiari—Lahore ±660kV HVDC Project Execution Sequence for Monopolar (Pole 1, Pole 2) Low Power Commissioning Tests
The test execution sequence will be as mentioned below.
Sr. No. | Test Block | Commissioning Items | Mode | Item Designations | Sub-item Designation | Power imported from AC Network
(MW)
DC Monopolar Point to Point Tests-Low Power
DC Station Tests must be successful before starting these tests
All tests in Test Block-LP1, LP2 should be executed in sequence as mentioned below. If any test fails in one block, next test item in the same block should not be executed however, next test block (Test Block-LP1,LP2) can be executed in the listed sequence.
Pole1 Low Power System Test, Normal Power Direction
Ground return mode
1 | Test Block-LP1 | 2.3.1 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Start /Stop Pole, Manual Block | 200
2 |  | 2.3.2 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Test of Emergency Stop | 200
3 |  | 2.3.3 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Control System Switchover | 200
4 |  | 2.3.4 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Pole Control, Analogue Input Check | 200
5 |  | 2.3.5 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | DC Side Protections, Analogue Input Check | 200
6 |  | 2.3.6 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | AC Side Protections, Analogue Input Check | 200
Metallic return mode
7 |  | 2.4.1 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Start /Stop Pole, Manual Block | 200
8 |  | 2.4.2 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Test of Emergency Stop | 200
9 |  | 2.4.3 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Control System Switchover | 200
10 |  | 2.4.4 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Pole Control, Analogue Input Check | 200
11 |  | 2.4.5 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | DC Side Protections, Analogue Input Check | 200
Pole2 Low Power System Test, Normal Power Direction
| Test Block-LP2 | Ground return mode
12 |  | 2.3.1 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Start /Stop Pole, Manual Block | 200
13 |  | 2.3.2 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Test of Emergency Stop | 200
14 |  | 2.3.3 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Control System Switchover | 200
15 |  | 2.3.4 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Pole Control, Analogue Input Check | 200
16 |  | 2.3.5 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | DC Side Protections, Analogue Input Check | 200
17 |  | 2.3.6 | GR | Initial Operation Tests, Joint Current Control, Normal Power Direction | AC Side Protections, Analogue Input Check | 200
Metallic return mode
18 |  | 2.4.1 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Start /Stop Pole, Manual Block | 200
19 |  | 2.4.2 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Test of Emergency Stop | 200
20 |  | 2.4.3 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Control System Switchover | 200
21 |  | 2.4.4 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | Pole Control, Analogue Input Check | 200
22 |  | 2.4.5 | MR | Initial Operation Tests, Joint Current Control, Normal Power Direction | DC Side Protections, Analogue Input Check | 200
DC Monopolar Low Power Protective Trip Testing
DC Tests from Sr. No. 01-22 must be successful before starting these tests
All tests in Test Block-LP3, LP4 may/may not be executed in sequence as mentioned below. If any test fails in one block, next test item in the same block can be executed however next test block (Test Block-LP4) cannot be executed until sucessful execution of Test Block 3.
Pole1 Low Power System Test
23 | Test Block-LP3 | 3.3.1 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip X in Rectifier with Telecommunication | 200
24 |  | 3.3.2 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip Y in Rectifier with Telecommunication | 200
25 |  | 3.3.3 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip Z in Rectifier with Telecommunication | 200
26 |  | 3.3.4 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip X in Inverter with Telecommunication | 200
27 |  | 3.3.5 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip Y in Inverter with Telecommunication | 200
28 |  | 3.3.6 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip Z in Inverter with Telecommunication | 200
29 |  | 3.3.7 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip Y in Rectifier without Telecommunication | 200
30 |  | 3.3.8 | GR | Protective Trip X, Y, and Z, Normal Power Direction | Protective Trip Y in Inverter without Telecommunication | 200
31 |  | 3.3.9 | GR | Protective Trip X, Y, and Z, Normal Power Direction | VBE Fault Protection Trip – Rectifier | 200
32 |  | 3.3.10 | GR | Protective Trip X, Y, and Z, Normal Power Direction | VBE Fault Protection Trip – Inverter | 200
33 |  | 4.3.1 | GR | System Supervision and Switchover | Active System Power Failure | 200
34 |  | 4.3.2 | GR | System Supervision and Switchover | Profibus bus Failure | 200
35 |  | 4.3.3 | GR | System Supervision and Switchover | LAN Bus Failure | 200
36 | Test Block-LP4 | 5.3.1 | GR | Steady State Operation, Joint Current Control, Normal Power Direction | Current Ramping and Hold on | 530
37 |  | 5.3.2 | GR | Steady State Operation, Joint Current Control, Normal Power Direction | System Switchover and Telecommunication Failure During Current Ramping | 330
38 |  | 5.3.3 | GR | Steady State Operation, Joint Current Control, Normal Power Direction | Tap Changer Control, Manual Tap Changer Stepping | 200
39 |  | 5.3.4 | GR | Steady State Operation, Joint Current Control, Normal Power Direction | Current Step Test | 330
40 |  | 5.3.5 | GR | Steady State Operation, Joint Current Control, Normal Power Direction | Voltage Step Test | 330
41 |  | 5.3.6 | GR | Steady State Operation, Joint Current Control, Normal Power Direction | Angle γ Step Test | 330
42 |  | 5.3.7 | GR | Steady State Operation, Joint Current Control, Normal Power Direction | Control Mode Shift, Current Margin Compensation | 330
43 |  | 6.3.1 | GR | Steady State Operation, Joint Power Control, Normal Power Direction | Start/Stop Pole | 200
44 |  | 6.3.2 | GR | Steady State Operation, Joint Power Control, Normal Power Direction | System Switchover and Telecommunication Failure During Power Ramping | 500
45 |  | 6.3.3 | GR | Steady State Operation, Joint Power Control, Normal Power Direction | Power Step Test | 400
46 |  | 6.3.4 | GR | Steady State Operation, Joint Power Control, Normal Power Direction | Control Mode Shift, Current Margin Compensation | 400
Monopolar Low Power Operational Tests
DC Tests from Sr. No. 23-46 must be successful before starting these tests
All tests in Test Block-LP5, LP6, LP7, LP8 should be executed in sequence as listed below. If any test fails in one block, next test item in the same block should not be executed however, next test block (Test Block-LP5,LP6,L LP7,LP8) can be executed in the listed sequence.
47 | Test Block-LP5 | 7.3.1 | GR | Normal Operation, Separate Current Control without Telecommunication | Start/Stop Pole | 200
48 |  | 7.3.2 | GR | Normal Operation, Separate Current Control without Telecommunication | System Switchover During Current Ramp | 330
49 |  | 8.3.1 | GR | Normal/Reduced Voltage, Normal Power Direction | Manual/Protection Triggering Reduced Voltage | 200
50 |  | 8.3.2 | GR | Normal/Reduced Voltage, Normal Power Direction | Power/Current Ramp | 400
51 | Test Block-LP6 | 9.3.1 | GR | Reactive Power Control, Normal Power Direction | Filter Requirement | 750
52 |  | 9.3.2 | GR | Reactive Power Control, Normal Power Direction | Filter Replacement | 200
53 |  | 9.3.3 | GR | Reactive Power Control, Normal Power Direction | Reactive Power Control | 400
54 |  | 9.3.4 | GR | Reactive Power Control, Normal Power Direction | Voltage Control | 400
55 |  | 9.3.5 | GR | Reactive Power Control, Normal Power Direction | Umax Control | 400
56 | Test Block-LP7 | 10.3.1 | GR/MR | Ground/Metallic Return Transfer | Ground/Metallic Return Transfer | 200
57 |  | 10.3.2 | GR/MR | Ground/Metallic Return Transfer | Metallic Return Operation With Station Ground at LAHORE Converter Station | 200
58 | Test Block-LP8 | 15.3.1 | GR | Backup Control | Monopole Start/Stop in Backup Panel | 200
59 |  | 15.3.2 | GR | Backup Control | Monopole Ramp up/down in Backup Panel | 400
DC Monopolar Low Power Tests -Reverse Power
All DC Low Power Tests in Normal Direction must be successful before starting these tests
All tests in Test Block-LP9, LP10, LP11 should be executed in sequence as listed below. If any test fails in one block, next test item in the same block should not be executed however, next test block (Test Block- LP10,LP11) can be executed in the prescribed sequence.
60 | Test Block-LP9 | 11.3.1 | GR | Initial Operation Tests, Ground Return Operation, Reversed Power Direction | Start/Stop Pole | 200
61 |  | 11.3.2 | GR | Initial Operation Tests, Ground Return Operation, Reversed Power Direction | Control System Switchover | 200
62 |  | 11.3.3 | GR/MR | Initial Operation Tests, Ground Return Operation, Reversed Power Direction | Ground/Metallic Return Transfer | 200
63 |  | 12.3.1 | MR | Joint Power Control, Metallic Return Operation, Reversed Power Direction | Start/Stop Pole, Joint Power Control | 200
64 |  | 12.3.2 | MR | Joint Power Control, Metallic Return Operation, Reversed Power Direction | Control System Switchover | 200
DC Monopolar Low Power Disturbance Tests
All tests above must be sucessful before executing these tests
65 | Test Block-LP10 | 14.3.1 | GR | Disturbances | DC Filter Switching | 200
66 |  | 14.3.2 | GR | Disturbances | Loss of 125V DC System C of Pole | 200
67 |  | 14.3.3 | GR | Disturbances | Loss of 125V DC System A of Pole | 300
68 |  | 14.3.4 | GR | Disturbances | Loss of 125V DC System B of Pole | 300
69 |  | 14.3.5 | GR | Disturbances | Simulated DC Line Fault (only Matiari) | 200
70 |  | 14.3.6 | GR | Disturbances | Simulate Fault of Converter Transformer PT Breaking at Matiari station | 200
71 |  | 14.3.7 | GR | Disturbances | Simulate Fault of Converter Transformer PT Breaking at LAHORE station | 200
72 |  | 14.3.8 | GR | Disturbances | Simulate Fault of DC Line PT Breaking at Matiari station | 200
73 |  | 14.3.9 | GR | Disturbances | Simulate Fault of DC Line PT Breaking at LAHORE station | 200
74 |  | 14.3.10 | GR | Disturbances | Simulate ACTIVE signal loss of pole control changeover device | 200
75 | Test Block-LP-11 | 13.3.1 | GR | Control Pulse Loss Failure, Normal Power Direction | Multiple (>5) Pulses Loss Fault at Inverter in Ground Return | 200
76 |  | 13.3.3 | GR | Control Pulse Loss Failure, Normal Power Direction | Multiple (>5) Pulses Loss Fault at Rectifier in Ground Return | 200
77 |  | 13.3.2 | MR | Control Pulse Loss Failure, Normal Power Direction | Multiple (>5) Pulses Loss Fault at Inverter in Metallic Return | 200
78 |  |  | MR | Control Pulse Loss Failure, Normal Power Direction | Multiple (>5) Pulses Loss Fault at Rectifier in Metallic Return | 200
Pole2 Low Power System Test (Protective Trip/Operational/Reverse Power/Disturbance)
Repeat Tests from Test No 23 to 78 for Pole-2
P2- 79-164 | LP3- LP-11

## IOT, GR
Monopole Low Power Tests
1-Initial Operation Tests, Joint Current Control, Normal Power Direction, Ground Return.
Test Objective | To verify the basic function of deblock/block, manually switchover and ESOF, and check the correctness and accuracy of analog signal of control and protection system.
Condition | Sr. No. | Station | Action | Equipment/ Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side switchyard status | During Pole-I testing
| 4 |  | See Status Table "P1-GR" |  |  | Ground Return Mode
| 5 |  | See Status Table "Mat-P2-ISOLAT" for Matiari and "Lah-P2-ISOLAT" for Lahore. |  |  | Isolation Mode
| 6 |  | During Pole-II testing
| 7 |  | See Status Table "Mat-P1-ISOLAT" for Matiari and "Lah-P1-ISOLAT" for Lahore. |  |  | Isolation Mode
| 8 |  | See Status Table "P2-GR" |  |  | Ground Return Mode
| 9 | General Preconditions | All the Prerequisites as mentioned in DC Dispatch Plan should be met.
| 10 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 11 |  | All electrical connections are available.
| 12 |  | Correct grounding of all equipment is available.
| 13 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 14 |  | Thyristor valves and valve hall is cleaned.
| 15 |  | Verify Sequence of Events Recorder (SER) and make sure that no relevant alarms are present, and all systems are operational.
Inter-station telecommunication check of control and protection signals
| 17 |  | Converter valve low voltage tests must be completed.
| 18 |  | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 19 |  | Air humidity and temperature in valve hall are within expected limits.
| 20 |  | Station Tests have been successful
| 21 |  | OLT with DC Line must be successful
| 22 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (200 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 23 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 24 |  | Return | Ground |  | Ground Return Mode
| 25 |  | Udc Mode | Normal |  | ±660kV
| 26 |  | Telecom Mode | Operational
| 27 |  | Master Station | Matiari
| 28 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 29 |  |  | B | Standby
| 30 |  | Pole Control (PCP) | A | ACTIVE
| 31 |  |  | B | Standby
| 32 |  | Transmission Control Mode | Current | ACTIVE | HVDC will operate in current control mode.
| 33 |  | Station Control Mode | Joint | ACTIVE | Matiari & Lahore will operate jointly.
| 34 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 35 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Pole Start/Stop Pole Manual Block (Sr. No. 1) | 36 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 37 | Matiari | Start the Pole | DC Current | 303 A [200 MW]
| 38 |  |  | Ramp Rate: | 100A/Min
| 39 |  | Wait to achieve Target Value | Max Time | 5 min
| 40 |  | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 41 |  |  | DC Voltages | 660kV
| 42 |  |  | RPC Operation | BP-11/13 , HP24/36
| 43 | Lahore |  | Extinction Angle (g) | 17°
| 44 |  |  | DC Voltages | Range to be mentioned
| 45 |  |  | RPC Operation | 1xHP12/24
| 46 | Matiari/Lahore | Verify stable operation at minimum current.
| 47 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 48 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 49 | Lahore |  | 1xHP12/24
| 50 | Matiari | Stop the Pole
| 51 |  | Verify Performance parameters | Retard, Reduced Current
| 52 | Lahore |  | Firing angle (α) | 90°
Test of Emergency stop (Sr. No. 2) | 53 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 54 | Matiari | Start the Pole | Current | 303 A [200 MW] | If pole is being operated at 200 MW ignore this step
| 55 |  |  | Ramp Rate: | 100A/Min
| 56 |  | Emergency Stop the Pole
| 57 |  | Verify Protection Functions | Y-block
| 58 |  |  | Trip Action | Converter T/F AC Breakers
| 59 |  |  |  | AC Filter Breakers by RPC
| 60 |  |  | Pole IsolationSequence
| 61 |  |  | Start Breaker Failure Protection
| 62 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 63 | Lahore |  | Normal Y-block sequence
| 64 |  |  | Trip of the AC Filters breakers by RPC
| 65 |  | Make sure, Master Station is selected |  |  | If pole is being operated at 200 MW ignore this step
| 66 |  | Verify Ready for Operation Conditions.
| 67 |  | Start the Pole | Current | 303 A [200 MW]
| 68 |  |  | Ramp Rate: | 100A/Min
| 69 |  | Emergency Stop the Pole
| 70 |  | Verify Protection Functions | Y-block
| 71 |  |  | Block Converter with By-Pass pair
| 72 |  |  | Trip | Converter T/F AC Breakers
| 73 |  |  |  | AC Filter Breakers by RPC
| 74 |  |  | Pole IsolationSequence
| 75 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 76 |  |  | Start Breaker Failure Protection
| 77 | Matiari |  | Normal Y-block sequence
| 78 |  |  | Trip of the AC Filters breakers by RPC
Control System Switchover (Sr. No. 3) | 79 | Matiari | Make sure, Master Station is selected |  |  | If pole is being operated at 200 MW ignore this step
| 80 |  | Verify Ready for Operation Conditions.
| 81 |  | Start the Pole-1 | Current | 303 A [200 MW]
| 82 |  |  | Ramp Rate: | 100A/Min
| 83 |  | Verify | PCP-A | ACTIVE
| 84 |  | Switch Control System | PCP-A to | PCP-B
| 85 |  | Verify | Continuous Steady Operation of the transmission
| 86 |  |  | PCP-B is active
| 87 |  |  | No Transients on switchover, no unexpectd Time Delay
| 88 |  | Switch Control System | PCP-B to | PCP-A
| 89 |  | Verify | Continuous Steady Operation of the transmission
| 90 |  |  | PCP-A is active
| 91 |  |  | No Transients on switchover, no unexpectd Time Delay
| 92 |  | Verify | SC-A | ACTIVE
| 93 |  | Switch Control System | SC-A | SC-B
| 94 |  | Verify | Continuous Steady Operation of the transmission
| 95 |  |  | SC-B is active
| 96 |  |  | No Transients on switchover, no unexpectd Time Delay
| 97 |  | Switch Control System | SC-B | SC-A
| 98 |  | Verify | Continuous Steady Operation of the transmission
| 99 |  |  | SC-A is active
| 100 |  |  | No Transients on switchover, no unexpectd Time Delay
Control System Switchover (Sr. No. 3) | 101 | Lahore | Verify | PCP-A | ACTIVE
| 102 |  | Switch Control System | PCP-A to | PCP-B
| 103 |  | Verify | Continuous Steady Operation of the transmission
| 104 |  |  | PCP-B is active
| 105 |  |  | No Transients on switchover, no unexpectd Time Delay
| 106 |  | Switch Control System | PCP-B to | PCP-A
| 107 |  | Verify | Continuous Steady Operation of the transmission
| 108 |  |  | PCP-A is active
| 109 |  |  | No Transients on switchover, no unexpectd Time Delay
| 110 |  | Verify | SC-A | ACTIVE
| 111 |  | Switch Control System | SC-A | SC-B
| 112 |  | Verify | Continuous Steady Operation of the transmission
| 113 |  |  | SC-B is active
| 114 |  |  | No Transients on switchover, no unexpectd Time Delay
| 115 |  | Switch Control System | SC-B | SC-A
| 116 |  | Verify | Continuous Steady Operation of the transmission
| 117 |  |  | SC-A is active
| 118 |  |  | No Transients on switchover, no unexpectd Time Delay
Pole Control. DC Side Protections AC Side Protections [Analogue Input Checks] (Sr. No. 4) | 119 |  | Make sure, Master Station is selected |  |  | If pole is being operated at 200 MW ignore this step
| 120 |  | Verify Ready for Operation Conditions.
| 121 | Matiari | Start the Pole | Current | 303 A [200 MW]
| 122 |  |  | Ramp Rate: | 100A/Min
| 123 |  | Inspect AC/DC analogue input signal of following systems while operating the pole at minimum power 303 Amps | Pole Control
| 124 |  |  | DC Side Protections
| 125 |  |  | AC Side Protections
| 126 | Lahore | Inspect AC/DC analogue input signal of following systems while operating the pole at minimum power 303 Amps | Pole Control
| 127 |  |  | DC Side Protections
| 128 |  |  | AC Side Protections
Test Acceptance Criteria | 129 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 130 |  | All Operations executed successfully
| 131 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 132 |  | All thyristor check-back signals are available.
| 133 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 134 |  | Measuring quantities are available and the values are within the specified range and phase.
| 135 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 136 |  | No Stuck Condition
| 137 |  | No False Tripping by DC Protection System
| 138 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 139 |  | No Tripping in AC side of converter Station

## IOT, MR
Monopole Low Power Tests
2-Initial Operation Tests, Joint Current Control, Normal Power Direction, Metallic return
Test Objective | To verify the basic function of deblock/block, manually switchover and ESOF, and check the correctness and accuracy of analog signal of control and protection system.
Condition | Sr. No. | Station | Action | Equipment/Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side switchyard status | During Pole-I testing
| 4 |  | See Status Table "P1-MR" |  |  | Metallic Return Mode
| 5 |  | See Status Table "Mat-P2-ISOLAT" for Matiari and "Lah-P2-ISOLAT" for Lahore. |  |  | Isolation Mode
| 6 |  | During Pole-II testing
| 7 |  | See Status Table "Mat-P1-ISOLAT" for Matiari and "Lah-P1-ISOLAT" for Lahore. |  |  | Isolation Mode
| 8 |  | See Status Table "P2-MR" |  |  | Metallic Return Mode
| 9 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 10 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 11 |  | All electrical connections are available.
| 12 |  | Correct grounding of all equipment is available.
| 13 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 14 |  | Thyristor valves and valve hall is cleaned.
| 15 |  | Verify Sequence of Events Recorder (SER) and make sure that no relevant alarms are present, and all systems are operational.
Inter-station telecommunication check of control and protection signals
| 17 |  | Converter valve low voltage tests must be completed.
| 18 |  | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 19 |  | Air humidity and temperature in valve hall are within expected limits.
| 20 |  | Initial Operation Tests in Ground Return Mode were successful.
| 21 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (200 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 22 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 23 |  | Return | Metallic |  | Metallic Return Mode
| 24 |  | Udc Mode | Normal |  | ±660kV
| 25 |  | Telecom Mode | Operational
| 26 |  | Master Station | Matiari
| 27 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 28 |  |  | B | Standby
| 29 |  | Pole Control (PCP) | A | ACTIVE
| 30 |  |  | B | Standby
| 31 |  | Transmission Control Mode | Current | ACTIVE | HVDC will operate in current control mode.
| 32 |  | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 33 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 34 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
| 35 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
Pole Start/Stop Pole Manual Block (Sr. No. 5) | 36 | Matiari | Start the Pole | Current | 303 A [200 MW]
| 37 |  |  | Ramp Rate: | 100A/Min
| 38 |  | Wait to achieve Target Value | Max Time | 5 min
| 39 |  | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 40 |  |  | DC Voltages | 660kV
| 41 |  |  | Valve Voltages | 660kV
| 42 |  |  | RPC Operation | BP-11/13 , HP24/36
| 43 | Lahore |  | Extinction Angle (g) | 17°
| 44 |  |  | DC Voltages | Range to be mentioned
| 45 |  |  | RPC Operation | 1xHP12/24
| 46 |  |  | Valve Currents | Range to be mentioned
| 47 |  |  | Valve Voltages | Range to be mentioned
| 48 | Matiari/Lahore | Verify stable operation at minimum current.
| 49 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 50 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 51 | Lahore |  | 1xHP-12/24
| 52 | Matiari | Stop the Pole
| 53 |  | Verify Performance parameters | Retard, Reduced Current
| 54 | Lahore |  | Firing angle | 90°
Test of Emergency stop | 55 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 56 | Matiari | Start the Pole | Current | 303 A [200 MW] | If pole is being operated at 200 MW ignore this step
| 57 |  |  | Ramp Rate: | 100A/Min
| 58 |  | Emergency Stop the Pole
| 59 |  | Verify Protection Functions | Y-block
| 60 |  |  | Trip Action | Converter T/F AC Breakers
| 61 |  |  |  | AC Filter Breakers by RPC
| 62 |  |  | Pole IsolationSequence
| 63 |  |  | Start Breaker Failure Protection
| 64 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 65 | Lahore |  | Normal Y-block sequence
| 66 |  |  | Trip of the AC Filters breakers by RPC
| 67 |  | Start the Pole | Current | 303 A [200 MW] | If pole is being operated at 200 MW ignore this step
| 68 |  |  | Ramp Rate: | 100A/Min
| 69 |  | Emergency Stop the Pole
| 70 |  | Verify Protection Functions | Y-block
| 71 |  |  | Block Converter with By-Pass pair
| 72 |  |  | Trip | Converter T/F AC Breakers
| 73 |  |  |  | AC Filter Breakers by RPC
| 74 |  |  | Pole IsolationSequence
| 75 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 76 | Matiari |  | Normal Y-block sequence
| 77 |  |  | Trip of the AC Filters breakers by RPC
Control System Switchover | 78 | Matiari | Make sure, Master Station is selected
| 79 |  | Verify Ready for Operation Conditions.
| 80 |  | Start the Pole | Current | 303 A [200 MW] | If pole is being operated at 200 MW ignore this step
| 81 |  |  | Ramp Rate: | 100A/Min
| 82 |  | Verify | PCP-A | ACTIVE
| 83 |  | Switch Control System | PCP-A to | PCP-B
| 84 |  | Verify | Continuous Steady Operation of the transmission
| 85 |  |  | PCP-B is active
| 86 |  |  | No Transients on switchover, no unexpectd Time Delay
| 87 |  | Switch Control System | PCP-B to | PCP-A
| 88 |  | Verify | Continuous Steady Operation of the transmission
| 89 |  |  | PCP-A is active
| 90 |  |  | No Transients on switchover, no unexpectd Time Delay
| 91 |  | Verify | SC-A | ACTIVE
| 92 |  | Switch Control System | SC-A | SC-B
| 93 |  | Verify | Continuous Steady Operation of the transmission
| 94 |  |  | SC-B is active
| 95 |  |  | No Transients on switchover, no unexpectd Time Delay
| 96 |  | Switch Control System | SC-B | SC-A
| 97 |  | Verify | Continuous Steady Operation of the transmission
| 98 |  |  | SC-A is active
| 99 |  |  | No Transients on switchover, no unexpectd Time Delay
Control System Switchover | 100 | Lahore | Verify | PCP-A | ACTIVE
| 101 |  | Switch Control System | PCP-A to | PCP-B
| 102 |  | Verify | Continuous Steady Operation of the transmission
| 103 |  |  | PCP-B is active
| 104 |  |  | No Transients on switchover, no unexpectd Time Delay
| 105 |  | Switch Control System | PCP-B to | PCP-A
| 106 |  | Verify | Continuous Steady Operation of the transmission
| 107 |  |  | PCP-A is active
| 108 |  |  | No Transients on switchover, no unexpectd Time Delay
| 109 |  | Verify | SC-A | ACTIVE
| 110 |  | Switch Control System | SC-A to | SC-B
| 111 |  | Verify | Continuous Steady Operation of the transmission
| 112 |  |  | SC-B is active
| 113 |  |  | No Transients on switchover, no unexpectd Time Delay
| 114 |  | Switch Control System | SC-B to | SC-A
| 115 |  | Verify | Continuous Steady Operation of the transmission
| 116 |  |  | SC-A is active
| 117 |  |  | No Transients on switchover, no unexpectd Time Delay
Pole Control. DC Side Protections AC Side Protections [Analogue Input Checks] | 118 | Matiari | Make sure, Master Station is selected |  |  | If pole is being operated at 200 MW ignore this step
| 119 |  | Verify Ready for Operation Conditions.
| 120 |  | Start the Pole | Current | 303 A [200 MW]
| 121 |  |  | Ramp Rate: | 100A/Min
| 122 |  | Inspect AC/DC analogue input signal of following systems while operating the pole at minimum power 303 Amps | Pole Control
| 123 |  |  | DC Side Protections
| 124 |  |  | AC Side Protections
| 125 | Lahore | Inspect AC/DC analogue input signal of following systems while operating the pole at minimum power 303 Amps | Pole Control
| 126 |  |  | DC Side Protections
| 127 |  |  | AC Side Protections
Test Acceptance Criteria | 128 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 129 |  | All Operations executed successfully
| 130 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 131 |  | All thyristor check-back signals are available.
| 132 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 133 |  | Measuring quantities are available and the values are within the specified range and phase.
| 134 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 135 |  | No Stuck Condition
| 136 |  | No False Tripping by DC Protection System
| 137 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 138 |  | No Tripping in AC side of converter Station
k

## Protective Trip XYZ +TCOM
Monopole Low Power Tests
3-Protective Trip X, Y, and Z, Joint Current Control, Normal Power Direction, Ground return
Test Objective | The test is carried on both sides and to check trip and block sequence.
Condition | Sr. No. | Station | Action | Equipment/Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side switchyard status | During Pole-I testing
| 4 |  | See Status Table "P1-GR" |  |  | Ground Return Mode
| 5 |  | See Status Table "Mat-P2-ISOLAT" for Matiari and "Lah-P2-ISOLAT" for Lahore. |  |  | Isolation Mode
| 6 |  | During Pole-II testing
| 7 |  | See Status Table "Mat-P1-ISOLAT" for Matiari and "Lah-P1-ISOLAT" for Lahore. |  |  | Isolation Mode
| 8 |  | See Status Table "P2-GR" |  |  | Ground Return Mode
| 9 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 10 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 11 |  | All electrical connections are available.
| 12 |  | Correct grounding of all equipment is available.
| 13 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 14 |  | Thyristor valves and valve hall is cleaned.
| 15 |  | Verify Sequence of Events Recorder (SER) and make sure that no relevant alarms are present, and all systems are operational.
Inter-station telecommunication check of control and protection signals
| 17 |  | Converter valve low voltage tests must be completed.
| 18 |  | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 19 |  | Air humidity and temperature in valve hall are within expected limits.
| 20 |  | Initial Operation Tests in Ground Return Mode of Pole-I and Pole-II must be successful.
| 21 |  | Initial Operation Tests in Metallic Return Mode of both Pole-I and Pole-II must be successful.
| 22 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (200 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 23 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 24 |  | Return | Ground |  | Ground Return Mode
| 25 |  | Udc Mode | Normal |  | ±660kV
| 26 |  | Telecom Mode | Operational
| 27 |  | Master Station | Matiari
| 28 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 29 |  |  | B | Standby
| 30 |  | Pole Control Protection (PCP) | A | ACTIVE
| 31 |  |  | B | Standby
| 32 |  | Transmission Control Mode | Current | ACTIVE | HVDC will operate in current control mode.
| 33 |  | Station Control Mode | Joint | ACTIVE | Matiari & Lahore will operate jointly.
| 34 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 35 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Protective Trip X in rectifier with TELECOM | 36 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions. |  |  | If pole is being operated at 200 MW ignore this step
| 37 | Matiari | Start the Pole | Current | 303 A [200 MW]
| 38 |  |  | Ramp Rate: | 100A/Min
| 39 |  | Instruct Test commander to Simulate Valve short Circuit Protection Stage 2 TRIP as mentioned in commissioning program.
| 40 |  | Verify Protection Functions | X-block
| 41 |  |  | Trip Action | Converter T/F AC Breakers
| 42 |  |  |  | AC Filter Breakers by RPC
| 43 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 44 |  |  | Start Breaker Failure Protection
| 45 |  |  | Pole IsolationSequence
| 46 | Lahore |  | Normal Y-STOP sequence
| 47 |  |  | Trip of the AC Filters breakers by RPC
Protective Trip Y in rectifier with TELECOM | 48 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions. |  |  | If pole is being operated at 200 MW ignore this step
| 49 | Matiari | Start the Pole | Current | 303 A [200 MW]
| 50 |  |  | Ramp Rate: | 100A/Min
| 51 |  | Verify | PUMP-A | ACTIVE
| 52 |  | Turn OFF | PUMP-A
| 53 |  | Verify | Continuous Steady Operation of the transmission
| 54 |  |  | PUMP-B is active
| 55 |  |  | No Transients
| 56 |  | Restore Supply of PUMP-A
| 57 |  | Turn OFF | PUMP-B
| 58 |  | Verify | Continuous Steady Operation of the transmission
| 59 |  |  | PUMP-A is active
| 60 |  |  | No Transients
| 61 |  | Turn OFF | PUMP-A
| 62 |  | Verify Protection Functions | Y-block
| 63 |  |  | Block Converter with By-Pass pair
| 64 |  |  | Trip | Converter T/F AC Breakers
| 65 |  |  |  | AC Filter Breakers by RPC
| 66 |  |  | Pole IsolationSequence
| 67 |  |  | Start Breaker Failure Protection
| 68 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 69 | Lahore |  | Normal Y-STOP sequence
| 70 |  |  | Trip of the AC Filters breakers by RPC
Protective Trip Z in rectifier with TELECOM | 71 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions. |  |  | If pole is being operated at 200 MW ignore this step
| 72 | Matiari | Start the Pole | Current | 303 A [200 MW]
| 73 |  |  | Ramp Rate: | 100A/Min
| 74 |  | Instruct Test Commander to Simulate Pole Bus Differential Protection Stage-2 Trip as mentioned in commissioning program.
| 75 |  | Verify Protection Functions | Z-block
| 76 |  |  | Trip Action | Converter T/F AC Breakers
| 77 |  |  |  | AC Filter Breakers by RPC
| 78 |  |  | Pole IsolationSequence
| 79 |  |  | Start Breaker Failure Protection
| 80 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 81 | Lahore |  | Normal Y-STOP sequence
| 82 |  |  | Trip of the AC Filters breakers by RPC
Protective Trip X in inverter with TELECOM | 83 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions. |  |  | If pole is being operated at 200 MW ignore this step
| 84 | Lahore | Start the Pole | Current | 303 A [200 MW]
| 85 |  |  | Ramp Rate: | 100A/Min
| 86 |  | Instruct Test commander to Simulate Valve short Circuit Protection Stage 2 TRIP as mentioned in commissioning program.
| 87 |  | Verify Protection Functions | X-block
| 88 |  |  | Block Converter with by pass pair
| 89 |  |  | Trip Action | AC circuit breaker(s) feeding the converter transformer
| 90 |  |  |  | AC Filter Breakers by RPC
| 91 |  |  | Pole IsolationSequence
| 92 |  |  | Start Breaker Failure Protection
| 93 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 94 | Matiari |  | Normal Y-stop sequence
| 95 |  |  | Trip of the AC Filters breakers by RPC
Protective Trip Y in inverter with TELECOM | 96 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions. |  |  | If pole is being operated at 200 MW ignore this step
| 97 | Lahore | Start the Pole | Current | 303 A [200 MW]
| 98 |  |  | Ramp Rate: | 100A/Min
| 99 |  | Verify | PUMP-A | ACTIVE
| 100 |  | Turn OFF | PUMP-A
| 101 |  | Verify | Continuous Steady Operation of the transmission
| 102 |  |  | PUMP-B is active
| 103 |  |  | No Transients
| 104 |  | Restore Supply of PUMP-A
| 105 |  | Turn OFF | PUMP-B
| 106 |  | Verify | Continuous Steady Operation of the transmission
| 107 |  |  | PUMP-A is active
| 108 |  |  | No Transients
| 109 |  | Turn OFF | PUMP-A
| 110 |  | Verify Protection Functions | Y-block
| 111 |  |  | Retard & Block Converter with By-Pass pair
| 112 |  |  | Trip Action | AC circuit breaker(s) feeding the converter transformer
| 113 |  |  |  | AC Filter Breakers by RPC
| 114 |  |  | Pole IsolationSequence
| 115 |  |  | Start Breaker Failure Protection
| 116 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 117 | Matiari |  | Normal Y-stop sequence
| 118 |  |  | Trip of the AC Filters breakers by RPC
Protective Trip Z in inverter with TELECOM | 119 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions. |  |  | If pole is being operated at 200 MW ignore this step
| 120 | Lahore | Start the Pole-1 | Current | 303 A [200 MW]
| 121 |  |  | Ramp Rate: | 100A/Min
| 122 |  | Instruct test director to Simulate Pole Bus Differential Protection Stage 2TRIP as mentioned in commissioning program.
| 123 |  | Verify Protection Functions | Z-block
| 124 |  |  | Block Converter with by pass pair
| 125 |  |  | Trip Action | AC circuit breaker(s) feeding the converter transformer
| 126 |  |  | Pole IsolationSequence
| 127 |  |  | Trip Action | AC Filter Breakers by RPC
| 128 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 129 |  |  | Start Breaker Failure Protection
| 130 | Matiari |  | Normal Y-stop sequence
| 131 |  |  | Trip of the AC Filters breakers by RPC
Protective Trip Y in rectifier without TELECOM | 132 | Matiari | Start the Pole | Current | 303 A [200 MW] | If pole is being operated at 200 MW ignore this step
| 133 |  |  | Ramp Rate: | 100A/Min
| 134 |  | Disable the telecommunication (both channels).
| 135 |  | Instruct test commander to Simulate Neutral Bus Capacitor Overcurrent Protection Action
| 136 |  | Verify Protection Functions | Y-block
| 137 |  |  | Trip Action | Converter T/F AC Breakers
| 138 |  |  |  | AC Filter Breakers
| 139 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 140 |  |  | Start Breaker Failure Protection
| 141 |  |  | Pole IsolationSequence
| 142 |  |  | Start Breaker Failure Protection
| 143 | Lahore |  | Trip from DC control monitoring function.
| 144 |  |  | Z-Block Order
| 145 |  |  | Pole Isolation
| 146 |  |  | Trip of the AC Filters breakers
| 147 | Matiari | Restore All Telecommunications
Protective Trip Y in inverter without TELECOM | 148 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions. |  |  | If pole is being operated at 200 MW ignore this step
| 149 | Lahore | Start the Pole | Current | 303 A [200 MW]
| 150 |  |  | Ramp Rate: | 100A/Min
| 151 |  | Disable the telecommunication (both channels).
| 152 |  | Instruct Test director to Simulate Neutral Bus Capacitor Overcurrent Protection Action as mentioned in commissioning program
| 153 |  | Verify Protection Functions | Y-block
| 154 |  |  | Retard and blocking of the converter with by-pass pair
| 155 |  |  | Trip Action | Converter T/F AC Breakers
| 156 |  |  |  | AC Filter Breakers by RPC
| 157 |  |  | Pole IsolationSequence
| 158 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 159 |  |  | Start Breaker Failure Protection
| 160 | Matiari |  | Trip Pole Undervoltage Protection .
| 161 |  |  | Y-Block Order
| 162 |  |  | Pole Isolation
| 163 |  |  | Trip of the AC Filters breakers by RPC
| 164 | Lahore | Restore All Telecommunications
VBE Fault Protection Trip in rectifier | 165 | Matiari | Verify | Both Sets of VBE | ACTIVE
| 166 |  |  | HVDC | BLOCKED
| 167 |  |  | Converter T/F | Energized
| 168 |  |  | VBE-A | ACTIVE
| 169 |  | Turn OFF | VBE-A
| 170 |  | Verify | Continuous Steady Operation of the transmission
| 171 |  |  | VBE-B is active
| 172 |  |  | No Transients on switchover, no unexpectd Time Delay
| 173 |  | Restore Supply of VBE-A
| 174 |  | Turn OFF | VBE-B
| 175 |  | Verify | Continuous Steady Operation of the transmission
| 176 |  |  | VBE-A is active
| 177 |  |  | No Transients on switchover, no unexpectd Time Delay
| 178 |  | Restore Supply of VBE-B
| 179 |  | Instruct test director to simulate the VBE Fault Trip in Pole as per commissioning program
| 180 |  | Verify Protection Functions | Y-block
| 181 |  |  | Trip | Converter T/F AC Breakers
| 182 |  |  | Start Breaker Failure Protection
| 183 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 184 |  |  | Pole IsolationSequence
| 185 | Lahore |  | Normal Y-STOP sequence |  | Order Firing angle 90o, then block with BPPO
VBE Fault Protection Trip in inverter | 186 | Lahore | Verify | Both Sets of VBE | ACTIVE
| 187 |  |  | HVDC | BLOCKED
| 188 |  |  | Converter T/F | Energized
| 189 |  |  | VBE-A | ACTIVE
| 190 |  | Turn OFF | VBE-A
| 191 |  | Verify | Continuous Steady Operation of the transmission
| 192 |  |  | VBE-B is active
| 193 |  |  | No Transients on switchover, no unexpectd Time Delay
| 194 |  | Restore Supply of VBE-A
| 195 |  | Turn OFF | VBE-B
| 196 |  | Verify | Continuous Steady Operation of the transmission
| 197 |  |  | VBE-A is active
| 198 |  |  | No Transients on switchover, no unexpectd Time Delay
| 199 |  | Restore Supply of VBE-B
| 200 |  | Instruct test director to simulate the VBE Fault Trip in Pole as per commissioning program
| 201 |  | Verify Protection Functions | Y-block
| 202 |  |  | Trip | Converter T/F AC Breakers
| 203 |  |  | Start Breaker Failure Protection
| 204 |  |  | Set lockout relay for the tripped AC circuit breaker(s)
| 205 |  |  | Pole IsolationSequence
| 206 | Matiari |  | Normal Y-STOP sequence |  | Order Firing angle 90o, then block with BPPO
Test Acceptance Criteria | 207 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 208 |  | All Operations executed successfully
| 209 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 210 |  | All thyristor check-back signals are available.
| 211 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 212 |  | Measuring quantities are available and the values are within the specified range and phase.
| 213 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 214 |  | No Stuck Condition
| 215 |  | No False Tripping by DC Protection System
| 216 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 217 |  | No Tripping in AC side of converter Station
k

## System Supervision and Switc (2
Monopole Low Power Tests
4-System Supervision & Switchover Joint Current Control, Normal Power Direction, Ground Return
Test Objective | The test objective is to check system supervision and control and protection system function when active system power failure ,main computer and profibus bus fault happen.
Condition | Sr. No. | Station | Action | Equipment/Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side switchyard status | During Pole-I testing
| 4 |  | See Status Table "P1-GR" |  |  | Ground Return Mode
| 5 |  | See Status Table "Mat-P2-ISOLAT" for Matiari and "Lah-P2-ISOLAT" for Lahore. |  |  | Isolation Mode
| 6 |  | During Pole-II testing
| 7 |  | See Status Table "Mat-P1-ISOLAT" for Matiari and "Lah-P1-ISOLAT" for Lahore. |  |  | Isolation Mode
| 8 |  | See Status Table "P2-GR" |  |  | Ground Return Mode
| 9 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 10 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 11 |  | All electrical connections are available.
| 12 |  | Correct grounding of all equipment is available.
| 13 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 14 |  | Thyristor valves and valve hall is cleaned.
| 15 |  | Verify Sequence of Events Recorder (SER) and make sure that no relevant alarms are present, and all systems are operational.
Inter-station telecommunication check of control and protection signals
| 17 |  | Converter valve low voltage tests must be completed.
| 18 |  | Air humidity and temperature in valve hall are within expected limits.
| 19 |  | Initial Operation Tests in Ground Return Mode of Pole-I and Pole-II must be successful.
| 20 |  | Initial Operation Tests in Metallic Return Mode of both Pole-I and Pole-II must be successful.
| 21 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (200 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 22 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 23 |  | Return | Ground |  | Ground Return Mode
| 24 |  | Udc Mode | Normal |  | ±660kV
| 25 |  | Telecom Mode | Operational
| 26 |  | Master Station | Matiari
| 27 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 28 |  |  | B | Standby
| 29 |  | Pole Control Protection (PCP) | A | ACTIVE
| 30 |  |  | B | Standby
| 31 |  | Transmission Control Mode | Current | ACTIVE | HVDC will operate in current control mode.
| 32 |  | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 33 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 34 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Active System Power Failure Test | 35 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions. |  |  | If pole is being operated at 200 MW ignore this step
| 36 | Matiari | Make sure Matiari is Master Station
| 37 |  | Start the Pole | Current | 303 A [200 MW]
| 38 |  |  | Ramp Rate: | 100A/Min
| 39 |  | Verify | PCP-A | ACTIVE
| 40 |  | Switch Off | PCP-A
| 41 |  | Verify | Continuous Steady Operation of the transmission
| 42 |  |  | PCP-B is active
| 43 |  |  | No Transients on switchover, no unexpectd Time Delay
| 44 |  | Switch On | PCP-A
| 45 |  | Restore PCP-A to StandBy Mode
| 46 |  | Switch Off | PCP-B
| 47 |  | Verify | Continuous Steady Operation of the transmission
| 48 |  |  | PCP-A is active
| 49 |  |  | No Transients on switchover, no unexpectd Time Delay
| 50 |  | Switch On | PCP-B
| 51 |  | Restore PCP-B to StandBy Mode
| 52 | Lahore | Start the Pole | Current | 303 A [200 MW] | If pole is being operated at 200 MW ignore this step
| 53 |  |  | Ramp Rate: | 100A/Min
| 54 |  | Verify | PCP-A | ACTIVE
| 55 |  | Switch Off | PCP-A
| 56 |  | Verify | Continuous Steady Operation of the transmission
| 57 |  |  | PCP-B is active
| 58 |  |  | No Transients on switchover, no unexpectd Time Delay
| 59 |  | Switch On | PCP-A
| 60 |  | Restore PCP-A to StandBy Mode
| 61 |  | Switch Off | PCP-B
| 62 |  | Verify | Continuous Steady Operation of the transmission
| 63 |  |  | PCP-A is active
| 64 |  |  | No Transients on switchover, no unexpectd Time Delay
| 65 |  | Switch On | PCP-B
| 66 |  | Restore PCP-B to StandBy Mode
Pole Profi Bus Failure | 67 | Matiari | Make sure Matiari is Master Station
| 68 |  | Start the Pole | Current | 303 A [200 MW] | If pole is being operated at 200 MW ignore this step
| 69 |  |  | Ramp Rate: | 100A/Min
| 70 |  | Provoke a Profibus failure | PCP-A
| 71 |  | Verify | Continuous Steady Operation of the transmission
| 72 |  |  | PCP-B is active
| 73 |  |  | No Transients on switchover, no unexpectd Time Delay
| 74 |  | Re-establish normal operation of main computer in PCPA
| 75 |  | Restore PCP-A to StandBy Mode
| 76 |  | Provoke a Profibus bus failure | PCP-B
| 77 |  | Verify | Continuous Steady Operation of the transmission
| 78 |  |  | PCP-A is active
| 79 |  |  | No Transients on switchover, no unexpectd Time Delay
| 80 |  | Re-establish normal operation of main computer in PCP-B
| 81 |  | Restore PCP-B to StandBy Mode
| 82 | Lahore | Make sure Lahore is Master Station |  |  | If pole is being operated at 200 MW ignore this step
| 83 |  | Start the Pole | Current | 303 A [200 MW]
| 84 |  |  | Ramp Rate: | 100A/Min
| 85 |  | Provoke a Profibus failure | PCP-A
| 86 |  | Verify | Continuous Steady Operation of the transmission
| 87 |  |  | PCP-B is active
| 88 |  |  | No Transients on switchover, no unexpectd Time Delay
| 89 |  | Re-establish normal operation of main computer in PCPA
| 90 |  | Restore PCP-A to StandBy Mode
| 91 |  | Provoke a Profibus bus failure | PCP-B
| 92 |  | Verify | Continuous Steady Operation of the transmission
| 93 |  |  | PCP-A is active
| 94 |  |  | No Transients on switchover, no unexpectd Time Delay
| 95 |  | Re-establish normal operation of main computer in PCP-B
| 96 |  | Restore PCP-B to StandBy Mode
Pole LAN Bus Failure | 97 | Matiari | Make sure Matiari is Master Station |  |  | If pole is being operated at 200 MW ignore this step
| 98 |  | Start the Pole | Current | 303 A [200 MW]
| 99 |  |  | Ramp Rate: | 100A/Min
| 100 |  | Provoke a Control LAN bus failure | PCP-A
| 101 |  | Verify | Continuous Steady Operation
| 102 |  |  | PCP-A is active
| 103 |  |  | ALARM
| 104 |  | Remove the second Control LAN bus
| 105 |  | Verify | Continuous Steady Operation of transmission
| 106 |  |  | PCP-B is active
| 107 |  |  | ]No transients on switchover, no unexpectd Time Delay
| 108 |  | Re-establish normal operation of main computer in PCPB
| 109 |  | Provoke a Control LAN bus failure | PCP-B
| 110 |  | Verify | Continuous Steady Operation
| 111 |  |  | PCP-B is active
| 112 |  |  | ALARM
| 113 |  | Remove the second Control LAN bus
| 114 |  | Verify | Continuous Steady Operation of the transmission
| 115 |  |  | PCP-A is active
| 116 |  |  | No Transients on switchover, no unexpectd Time Delay
| 117 |  | Re-establish normal operation of main computer in PCP-B
| 118 | Lahore | Make sure Lahore is Master Station |  |  | If pole is being operated at 200 MW ignore this step
| 119 |  | Start the Pole | Current | 303 A [200 MW]
| 120 |  |  | Ramp Rate: | 100A/Min
| 121 |  | Provoke a Control LAN bus failure | PCP-A
| 122 |  | Verify | Continuous Steady Operation
| 123 |  |  | PCP-A is active
| 124 |  |  | ALARM
| 125 |  | Remove the second Control LAN bus
| 126 |  | Verify | Continuous Steady Operation of transmission
| 127 |  |  | PCP-B is active
| 128 |  |  | No transients on switchover, no unexpectd Time Delay
| 129 |  | Re-establish normal operation of main computer in PCPB
| 130 |  | Provoke a Control LAN bus failure | PCP-B
| 131 |  | Verify | Continuous Steady Operation
| 132 |  |  | PCP-B is active
| 133 |  |  | ALARM
| 134 |  | Remove the second Control LAN bus
| 135 |  | Verify | Continuous Steady Operation of the transmission
| 136 |  |  | PCP-A is active
| 137 |  |  | No Transients on switchover, no unexpectd Time Delay
| 138 |  | Re-establish normal operation of main computer in PCP-B
Test Acceptance Criteria | 139 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 140 |  | All Operations executed successfully
| 141 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 142 |  | All thyristor check-back signals are available.
| 143 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 144 |  | Measuring quantities are available and the values are within the specified range and phase.
| 145 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 146 |  | No Stuck Condition
| 147 |  | No False Tripping by DC Protection System
| 148 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 149 |  | No Tripping in AC side of converter Station
k

## Steady State Operations, I
Monopole Low Power Tests
5-Steady State Operation Joint Current Control, Normal Power Direction, Ground return
Test Objective | The test is carried on both sides and to check trip and block sequence.
Condition | Sr. No. | Station | Action | Equipment/Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side switchyard status | During Pole-I testing
| 4 |  | See Status Table "P1-GR" |  |  | Ground Return Mode
| 5 |  | See Status Table "Mat-P2-ISOLAT" for Matiari and "Lah-P2-ISOLAT" for Lahore. |  |  | Isolation Mode
| 6 |  | During Pole-II testing
| 7 |  | See Status Table "Mat-P1-ISOLAT" for Matiari and "Lah-P1-ISOLAT" for Lahore. |  |  | Isolation Mode
| 8 |  | See Status Table "P2-GR" |  |  | Ground Return Mode
| 9 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 10 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 11 |  | All electrical connections are available.
| 12 |  | Correct grounding of all equipment is available.
| 13 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 14 |  | Thyristor valves and valve hall is cleaned.
| 15 |  | Verify Sequence of Events Recorder (SER) and make sure that no relevant alarms are present, and all systems are operational.
Inter-station telecommunication check of control and protection signals
| 17 |  | Converter valve low voltage tests must be completed.
| 18 |  | Air humidity and temperature in valve hall are within expected limits.
| 19 |  | Protective Trip X, Y, Z test in Normal Power Direction with Grount Return Mode (Annex-C-3 have been successful)
| 20 |  | System Supervision and Switchover in Normal Power Direction with Ground Return Mode (Annex-C-4 have been successful)
| 21 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (530 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 22 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 23 |  | Return | Ground |  | Ground Return Mode
| 24 |  | Udc Mode | Normal |  | ±660kV
| 25 |  | Telecom Mode | Operational
| 26 |  | Master Station | Matiari
| 27 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 28 |  |  | B | Standby
| 29 |  | Pole Control Protection (PCP) | A | ACTIVE
| 30 |  |  | B | Standby
| 31 |  | Transmission Control Mode | Current | ACTIVE | HVDC will operate in current control mode.
| 32 |  | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 33 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 34 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Pole Current Ramping and Holding On | 35 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions. |  |  | If pole is being operated at 200 MW ignore this step
| 36 | Matiari | Start the Pole | Current | 303 A [200 MW]
| 37 |  |  | Ramp Rate: | 100A/Min
| 38 |  | Ramp Up | 303A | 500A | 100A/Min
| 39 |  | Verify | Ramping at correct ramp rate
| 40 |  |  | No Transients, no unexpectd Time Delay
| 41 |  | Order STOP Ramp
| 42 |  | Verify | Ramp stopped, holding stopped value
| 43 |  |  | No Transients, no unexpected Time Delay
| 44 | Lahore | Transfer the MASTER station | TO LAHORE
| 45 |  | Ramp Up | Stopped Ramp Value | 500A | 100A/Min
| 46 |  | Verify | Ramping at correct ramp rate
| 47 |  |  | Continuous Steady Operation
| 48 |  |  | Ramping Done and Holding the target Value
| 49 |  |  | No Transients, no unexpected Time Delay
| 50 |  | NPCC makes sure, parallel AC corridor has margin for sharing 200 MW with DC System. (Sudden load sharing from AC corridor to DC corridor will happen in next step)
| 51 |  | Ramp Up | 500A | 800A | 999A/Min
| 52 |  | Verify | Ramping at correct ramp rate
| 53 |  |  | Continuous Steady Operation
| 54 |  |  | Ramping Done and Holding the target Value
| 55 |  |  | No Transients, no unexpected Time Delay
| 56 |  | NPCC makes sure, parallel AC corridor has margin for sharing 200 MW with DC System. (Sudden load sharing from AC corridor to DC corridor will happen in next step)
| 57 |  | Ramp Down | 800A | 500A | 999A/Min
| 58 |  | Verify | Ramping at correct ramp rate
| 59 |  |  | Continuous Steady Operation
| 60 |  |  | Ramping Done and Holding the target Value
| 61 |  |  | No Transients, no unexpectd Time Delay
| 62 |  | Confirm Lahore is MASTER station.
| 63 |  | Ramp Down | 500A | 303A | 100A/Min
| 64 |  | Verify | Ramping at correct ramp rate
| 65 |  |  | No Transients, no unexpected Time Delay
| 66 |  | Order STOP Ramp
| 67 |  | Verify | Ramp stopped, holding stopped value
| 68 |  |  | No Transients, no unexpected Time Delay
| 69 | Matiari | Transfer the MASTER station | TO Matiari
| 70 |  | Ramp Down | Stopped Ramp Value | 303A | 100A/Min
| 71 |  | Verify | Continuous Steady Operation
| 72 |  |  | Ramping Done and Holding the target Value
| 73 |  |  | No Transients, no unexpectd Time Delay
| 74 |  | NPCC makes sure, parallel AC corridor has margin for sharing 200 MW with DC System. (Sudden load sharing from AC corridor to DC corridor will happen in next step)
| 75 |  | Ramp Up | 303A | 500A | 999A/Min
| 76 |  | Verify | Continuous Steady Operation
| 77 |  |  | Ramping Done and Holding the target Value
| 78 |  |  | No Transients, no unexpectd Time Delay
| 79 |  | NPCC makes sure, parallel AC corridor has margin for sharing 200 MW with DC System. (Sudden load sharing from AC corridor to DC corridor will happen in next step)
| 80 |  | Ramp Down | 500A | 303A | 999A/Min
| 81 |  | Verify | Continuous Steady Operation
| 82 |  |  | Ramping Done and Holding the target Value
| 83 |  |  | No Transients, no unexpectd Time Delay
Pole System Switch over and Telecommunication Failure During Current Ramping | 84 | Lahore | Confirm Lahore is Master Station
| 85 |  | Start the Pole | Current | 303 A [200 MW] | If pole is being operated at 200 MW ignore this step
| 86 |  |  | Ramp Rate: | 100A/Min
| 87 |  | Ramp Up | 303A | 500A | 50A/Min
| 88 |  | Manual Switch Over during Ramp up | PCP-A | PCP-B
| 89 |  |  | PCP-B | PCP-A
| 90 |  | Verify during ramping | Continuous Steady Operation
| 91 |  |  | No Transients, no unexpectd Time Delay
| 92 |  | Order TRANSFER TO POWER CONTROL while ramping
| 93 |  | Verify | No transfer to power control
| 94 |  |  | Ramping Done and Holding the target Value
| 95 |  |  | No transient change in current
| 96 | Matiari | Initiate the sequence of MASTER station.
| 97 |  | Ramp Down | 500A | 303A | 50A/Min
| 98 |  | Manual Switch Over during Ramp down | PCP-A | PCP-B
| 99 |  |  | PCP-B | PCP-A
| 100 |  | Disabled the telecommunication in both channels during the ramping process.
| 101 |  | Verify | Continuous Steady Operation
| 102 |  |  | Ramping Done and Holding the target Value
| 103 |  |  | Emergency Current Control mode would be automatically activated. |  | The ramping rate would be reduced but the ramp would continuing and the current reference value would be reached when the telecommunication is disabled,
| 104 |  | Restore the telecommunication.
Pole Tap Changer Control, Manual Tap Changer Stepping | 105 | Matiari | Start the Pole | Current | 303 A [200 MW] | If pole is being operated at 200 MW ignore this step
| 106 |  |  | Ramp Rate: | 100A/Min
| 107 |  | Set tap changer control in MANUAL CONTROL mode
| 108 |  | Raise two steps for increasing Udi0.
| 109 |  | Verify | Firing Angle Increased
| 110 |  |  | Transmitted Current is maintained
| 111 |  |  | No Transients, no unexpectd Time Delay
| 112 |  | Set tap changer control in AUTO CONTROL mode
| 113 |  | Verify | Tap decreased automatically
| 114 |  |  | Firing Angle Increased
| 115 |  |  | Transmitted Current is maintained
| 116 |  |  | No Transients, no unexpectd Time Delay
| 117 | Lahore | Set tap changer control in MANUAL CONTROL mode
| 118 |  | Lower two steps for increasing Udi0.
| 119 |  | Verify | Decreased DC Voltages
| 120 |  |  | Maintained Gamma in Lahore
| 121 |  |  | Transmitted Current is maintained
| 122 |  |  | No Transients, no unexpectd Time Delay
| 123 |  | Set tap changer control in AUTO CONTROL mode
| 124 |  | Verify | Tap increased automatically
| 125 |  |  | Firing Angleback in control limits
| 126 |  |  | DC Voltage back to normal
| 127 |  |  | Transmitted Current is maintained
| 128 |  |  | No Transients, no unexpectd Time Delay
Current Step Test | 129 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 130 | Matiari | Start the Pole | Current | 303 A [200 MW] | If pole is being operated at 200 MW ignore this step
| 131 |  |  | Ramp Rate: | 100A/Min
| 132 |  | Ramp Up | 303A | 500A | 100A/Min
| 133 |  | Instruct Test Commander to apply a +0.08 P.U Step in current Order with duration of 1000 msec in active PCP system.
| 134 |  | Record the current response and the overshoot, make sure the overshoot doesnot exceeds XX Value |  |  | XX value to be determined verified later with DPS studies
| 135 |  | Change all the modified settings back to original value
| 136 |  | Record and save all test dat
Voltage Step Test | 137 | Matiari | Start the Pole | Current | 303 A [200 MW] | If pole is being operated at 200 MW ignore this step
| 138 |  |  | Ramp Rate: | 100A/Min
| 139 |  | Ramp Up | 303A | 500A | 100A/Min
| 140 | Lahore | Instruct Test Commander to apply a -10% P.U Step in Voltage Order with duration of 1000 msec in active PCP system.
| 141 |  | Record the voltage response and the overshoot, make sure the overshoot doesnot exceeds XX Value |  |  | XX value to be determined verified later with DPS studies
| 142 |  | Change all the modified settings back to original value
| 143 |  | Record and save all test dat
Angle γ Step Test Step Test | 144 | Matiari | Start the Pole | Current | 303 A [200 MW] | If pole is being operated at 200 MW ignore this step
| 145 |  |  | Ramp Rate: | 100A/Min
| 146 |  | Ramp Up | 303A | 500A | 100A/Min
| 147 | Lahore | Instruct Test Commander to apply a +10% deg. Step in Extinction Angle with duration of 1000 msec in active PCP system.
| 148 |  | Record the extinction angle response and the overshoot, make sure the overshoot doesnot exceeds XX Value |  |  | XX value to be determined verified later with DPS studies
| 149 |  | Change all the modified settings back to original value
| 150 |  | Record and save all test dat
Control Mode Shift, Current Margin Compensation | 151 | Matiari | Start the Pole-1 | Current | 303 A [200 MW] | If pole is being operated at 200 MW ignore this step
| 152 |  |  | Ramp Rate: | 100A/Min
| 153 |  | Ramp Up | 303A | 500A | 100A/Min
| 154 | Matiari/Lahore | Set tap changer control in MANUAL CONTROL mode
| 155 | Matiari | Force a control mode shift by decreasing the tap changer until the inverter starts to control current
| 156 |  | Verify | Alarm(CMC active warning)
| 157 |  |  | Transmitted Current is maintained
| 158 |  |  | Firing angle in Matiari at the minimum value
| 159 |  |  | No Transients, no unexpectd Time Delay
| 160 | Lahore | Verify | The symbol ‘DCON200/YCS’in PCP/CPU5/E05_CC_C1/Page 16 software page in LAHORE is turned to be 2.
| 161 |  |  | The symbol ‘CMC200/Y’ in PCP/CPU3/C03_COC_PC/Page 5 software page in LAHORE turn to be ‘0.1p.u.’.
| 162 |  |  | Transmitted Current is maintained
| 163 |  |  | Current order is increased to compensate the current margin.
| 164 |  |  | No Transients, no unexpectd Time Delay
| 165 | Matiari/Lahore | Set tap changer control in AUTO CONTROL mode
| 166 |  | Verify | Tap increased automatically
| 167 |  |  | Firing Angleback in control limits
| 168 |  |  | DC Voltage back to normal
| 169 |  |  | Transmitted Current is maintained
| 170 |  |  | No Transients, no unexpectd Time Delay
| 171 | Matiari | Ramp Down | 500A | 303A | 100A/Min
| 172 | Matiari/Lahore | Record and save all test dat
Test Acceptance Criteria | 173 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 174 |  | All Operations executed successfully
| 175 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 176 |  | All thyristor check-back signals are available.
| 177 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 178 |  | Measuring quantities are available and the values are within the specified range and phase.
| 179 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 180 |  | No Stuck Condition
| 181 |  | No False Tripping by DC Protection System
| 182 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 183 |  | No Tripping in AC side of converter Station
k
Note on C41: PK: Please note that this test is not following the CET A3 test procedures. Modifications have been made to align dispatch procedure to test procedure.
Note on D67: PK: Lahore is already the Master Station

## Steady State Operations, P
Monopole Low Power Tests
6-Steady State Operation Joint Power Control, Normal Power Direction, Ground return
Test Objective | The test is carried on both sides and to check trip and block sequence.
Condition | Sr. No. | Station | Action | Equipment/Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side switchyard status | During Pole-I testing
| 4 |  | See Status Table "P1-GR" |  |  | Ground Return Mode
| 5 |  | See Status Table "Mat-P2-ISOLAT" for Matiari and "Lah-P2-ISOLAT" for Lahore. |  |  | Isolation Mode
| 6 |  | During Pole-II testing
| 7 |  | See Status Table "Mat-P1-ISOLAT" for Matiari and "Lah-P1-ISOLAT" for Lahore. |  |  | Isolation Mode
| 8 |  | See Status Table "P2-GR" |  |  | Ground Return Mode
| 9 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 10 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 11 |  | All electrical connections are available.
| 12 |  | Correct grounding of all equipment is available.
| 13 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 14 |  | Thyristor valves and valve hall is cleaned.
| 15 |  | Verify Sequence of Events Recorder (SER) and make sure that no relevant alarms are present, and all systems are operational.
Inter-station telecommunication check of control and protection signals
| 17 |  | Converter valve low voltage tests must be completed.
| 18 |  | Air humidity and temperature in valve hall are within expected limits.
| 19 |  | Steady State Operation Tests (current Control Mode) in Normal Power Direction with Ground Return Mode (Annex-C-5 must be successful)
| 20 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (500 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 21 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 22 |  | Return | Ground |  | Ground Return Mode
| 23 |  | Udc Mode | Normal |  | ±660kV
| 24 |  | Telecom Mode | Operational
| 25 |  | Master Station | Matiari
| 26 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 27 |  |  | B | Standby
| 28 |  | Pole Control Protection (PCP) | A | ACTIVE
| 29 |  |  | B | Standby
| 30 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 31 |  | Station Control Mode | Joint | Active | Matiari & Lahore will operate jointly.
| 32 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 33 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Pole Start/Stop Pole | 34 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 35 | Matiari | Start the Pole | Power | 200 MW
| 36 |  |  | Ramp Rate: | 50MW/Min
| 37 |  | Wait to achieve Target Value | Max Time | 5 min
| 38 |  | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 39 |  |  | DC Voltages | 660kV
| 40 |  |  | RPC Operation | BP-11/13 , HP24/36
| 41 | Lahore |  | Extinction Angle (g) | 17°
| 42 |  |  | DC Voltages | Range to be mentioned
| 43 |  |  | RPC Operation | 1xHP12/24
| 44 | Matiari/Lahore | Verify stable operation at minimum power
| 45 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 46 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 47 | Lahore |  | 1xHP12/24
| 48 | Matiari | Stop the Pole
| 49 |  | Verify Performance parameters | Retard, Reduced Current
| 50 | Lahore |  | Firing angle | 90°
Pole System Switch over and Telecommunication Failure During Power Ramping | 51 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 52 | Matiari | Start the Pole | Power | 200 MW
| 53 |  |  | Ramp Rate: | 50 MW/Min
| 54 |  | Ramp Up | 200 MW | 400 MW | 50 MW/Min
| 55 |  | Manual Switch Over during Ramp up | PCP-A to | PCP-B
| 56 |  | Manual Switch Over during Ramp up | PCP-B to | PCP-A
| 57 |  | Verify | Ramping at correct ramp rate
| 58 |  |  | No Transients, no unexpectd Time Delay
| 59 |  | Order STOP Ramping while ramping
| 60 |  | Verify | Ramping Stopped smoothly
| 61 |  |  | No Transients, no unexpectd Time Delay
| 62 | Lahore | Initiate the sequence of MASTER station at Lahore.
| 63 |  | Ramp Up | From stopped value | 400 MW | 50 MW/Min
| 64 |  | Order TRANSFER TO Current CONTROL while ramping
| 65 |  | Verify | no transfer during the power ramping
| 66 |  |  | no transient change in power
| 67 |  | NPCC makes sure, parallel AC corridor has margin for sharing 200 MW with DC System. (Sudden load sharing from AC corridor to DC corridor will happen in next step)
| 68 |  | Ramp Up | 400 MW | 500 MW | 999 MW/Min
| 69 |  | Verify | Continuous Steady Operation
| 70 |  |  | Ramping Done and Holding the target Value
| 71 |  |  | No Transients, no unexpected Time Delay
| 72 |  | NPCC makes sure, parallel AC corridor has margin for sharing 100 MW with DC System. (Sudden load sharing from AC corridor to DC corridor will happen in next step)
| 73 |  | Ramp Down | 500 MW | 400 MW | 999 MW/Min
| 74 |  | Verify | Continuous Steady Operation
| 75 |  |  | Ramping Done and Holding the target Value
| 76 |  |  | No Transients, no unexpectd Time Delay
| 77 |  | Confirm Lahore is Master Station
| 78 |  | Ramp Up Down | 400 MW | 200 MW | 50 MW/Min
| 79 |  | Manual Switch Over during Ramp down | PCP-A to | PCP-B
| 80 |  |  | PCP-B to | PCP-A
| 81 |  | Verify | Ramping at correct ramp rate
| 82 |  |  | No Transients, no unexpectd Time Delay
| 83 |  | Order STOP Ramping while ramping
| 84 |  | Verify | Ramping Stopped smoothly
| 85 |  |  | No Transients, no unexpectd Time Delay
| 86 |  | Ramp Down | From stopped value | 200 MW | 50 MW/Min
| 87 |  | Verify | Continuous Steady Operation
| 88 |  |  | Ramping Done and Holding the target Value
| 89 |  | NPCC makes sure, parallel AC corridor has margin for sharing 200 MW with DC System. (Sudden load sharing from AC corridor to DC corridor will happen in next step)
| 90 |  | Ramp Up | 200 MW | 400 MW | 999 MW/Min
| 91 |  | Verify | Continuous Steady Operation
| 92 |  |  | Ramping Done and Holding the target Value
| 93 |  |  | No Transients, no unexpectd Time Delay
| 94 |  | NPCC makes sure, parallel AC corridor has margin for sharing 200 MW with DC System. (Sudden load sharing from AC corridor to DC corridor will happen in next step)
| 95 |  | Ramp Down | 400 MW | 200 MW | 999 MW/Min
| 96 |  | Verify | Continuous Steady Operation
| 97 |  |  | Ramping Done and Holding the target Value
| 98 |  |  | No Transients, no unexpectd Time Delay
Pole System Switch over and Telecommunication Failure During Power Ramping | 99 | Matiari | Make sure Matiari is MASTER station.
| 100 |  | Ramp Up | 200 MW | 400 MW | 50 MW/Min
| 101 |  | Disabled the telecommunication in both channels during the ramping process.
| 102 |  | Verify | BSC mode is automatically activated & ramping continues
| 103 |  |  | Ramping Done and Holding the target Value
| 104 |  |  | No Transients, no unexpectd Time Delay
| 105 |  | Ramp Down | 400 MW | 200 MW | 50 MW/Min
| 106 |  | Restore the telecommunication while ramping down
| 107 |  | Verify | Ramping continues when telecommunication restored
| 108 |  |  | Ramping Done and Holding the target Value
| 109 |  |  | No Transients, no unexpectd Time Delay
Power Step Test | 110 | Matiari | Start the Pole | Power | 200 MW
| 111 |  |  | Ramp Rate: | 50MW/Min
| 112 |  | Ramp Up | 200 MW | 400 MW | 50 MW /min
| 113 |  | Instruct Test Commander to apply a +0.08 P.U Step in Power Order with duration of 1000 msec in active PCP system.
| 114 |  | Record the power response and the overshoot, make sure the overshoot doesnot exceeds XX Value
| 115 |  | Change all the modified settings back to original value
| 116 |  | Record and save all test dat
Control Mode Shift, Current Margin Compensation | 117 | Matiari | Start the Pole | Power | 200 MW
| 118 |  |  | Ramp Rate: | 50MW/Min
| 119 |  | Ramp Up | 200 MW | 400 MW | 50 MW /min
| 120 | Matiari/Lahore | Set tap changer control in MANUAL CONTROL mode
| 121 | Matiari | Force a control mode shift by decreasing the tap changer until the inverter starts to control current
| 122 |  | Verify | Alarm(CMC active warning)
| 123 |  |  | Transmitted Current is maintained
| 124 |  |  | Firing angle in Matiari at the minimum value
| 125 |  |  | No Transients, no unexpectd Time Delay
| 126 | Lahore | Verify | The symbol ‘DCON200/YCS’in PCP/CPU5/E05_CC_C1/Page 16 software page in LAHORE is turned to be 2.
| 127 |  |  | The symbol ‘CMC200/Y’ in PCP/CPU3/C03_COC_PC/Page 5 software page in LAHORE turn to be ‘0.1p.u.’.
| 128 |  |  | Transmitted Current is maintained
| 129 |  |  | Current order is increased to compensate the current margin.
| 130 |  |  | No Transients, no unexpectd Time Delay
| 131 | Matiari/Lahore | Set tap changer control in AUTO CONTROL mode
| 132 |  | Verify | Tap increased automatically
| 133 |  |  | Firing Angle back in control limits
| 134 |  |  | DC Voltage back to normal
| 135 |  |  | Transmitted Current is maintained
| 136 |  |  | No Transients, no unexpectd Time Delay
| 137 | Matiari | Ramp Down | 400 MW | 200 MW | 50 MW/Min
| 138 | Matiari/Lahore | Record and save all test dat
Test Acceptance Criteria | 139 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 140 |  | All Operations executed successfully
| 141 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 142 |  | All thyristor check-back signals are available.
| 143 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 144 |  | Measuring quantities are available and the values are within the specified range and phase.
| 145 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 146 |  | No Stuck Condition
| 147 |  | No False Tripping by DC Protection System
| 148 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 149 |  | No Tripping in AC side of converter Station
k

## Normal Operations, I-TCOM
Monopole Low Power Tests
7-Normal Operation Separate Current Control without Telecom, Ground return
Test Objective | The test objective is to check control system performance under BSC control mode.
Condition | Sr. No. | Station | Action | Equipment/Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side switchyard status | During Pole-I testing
| 4 |  | See Status Table "P1-GR" |  |  | Ground Return Mode
| 5 |  | See Status Table "Mat-P2-ISOLAT" for Matiari and "Lah-P2-ISOLAT" for Lahore. |  |  | Isolation Mode
| 6 |  | During Pole-II testing
| 7 |  | See Status Table "Mat-P1-ISOLAT" for Matiari and "Lah-P1-ISOLAT" for Lahore. |  |  | Isolation Mode
| 8 |  | See Status Table "P2-GR" |  |  | Ground Return Mode
| 9 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 10 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 11 |  | All electrical connections are available.
| 12 |  | Correct grounding of all equipment is available.
| 13 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 14 |  | Thyristor valves and valve hall is cleaned.
| 15 |  | Verify Sequence of Events Recorder (SER) and make sure that no relevant alarms are present, and all systems are operational.
Inter-station telecommunication check of control and protection signals
| 17 |  | Converter valve low voltage tests must be completed.
| 18 |  | Air humidity and temperature in valve hall are within expected limits.
| 19 |  | Steady State Operation Tests (Power Control Mode) in Normal Power Direction with Ground Return Mode (Annex-C-6 must be successful)
| 20 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (330 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 21 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 22 |  | Return | Ground |  | Ground Return Mode
| 23 |  | Udc Mode | Normal |  | ±660kV
| 24 |  | Telecom Mode | Operational
| 25 |  | Master Station | Matiari
| 26 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 27 |  |  | B | Standby
| 28 |  | Pole Control Protection (PCP) | A | ACTIVE
| 29 |  |  | B | Standby
| 30 |  | Transmission Control Mode | Current | ACTIVE | HVDC will operate in power control mode.
| 31 |  | Station Control Mode | Seperate | Active | Matiari & Lahore will operate jointly.
| 32 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 33 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Pole Start/Stop Pole | 34 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 35 | Matiari & Lahore | Disabled the telecommunication in both channels .
| 36 | Matiari & Lahore | Start the Pole, (By phone) [De-Block Inverter First Then De-Block Rectifier] | Current | 303 Amps
| 37 |  |  | Ramp Rate: | 100 A/Min
| 38 |  | Wait to achieve Target Value | Max Time | 5 min
| 39 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 40 |  |  | DC Voltages | 660kV
| 41 |  |  | RPC Operation | BP-11/13 , HP24/36
| 42 | Lahore |  | Extinction Angle (g) | 17°
| 43 |  |  | DC Voltages | Range to be mentioned
| 44 |  |  | RPC Operation | 1xHP12/24
| 45 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 46 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 47 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 48 | Lahore |  | 1xHP12/24
| 49 | Matiari/Lahore | Stop the Pole (By phone) [Block Rectifier First Then Block Inverter]
| 50 |  | Verify Performance parameters | Retard, Reduced Current
| 51 | Lahore |  | Firing angle (α) | 90°
Pole System Switch over During Current Ramping w/o Telecom | 52 | Matiari/Lahore C/S DC side | Make sure communication is disabled.
| 53 | Matiari / Lahore | Start the Pole-1, (By phone) [De-Block Inverter First Then De-Block Rectifier] | Current | 303 Amps
| 54 |  |  | Ramp Rate: | 100 A/Min
| 55 | Matiari | Ramp Up | 303 Amps | 500 Amps | 100 A/Min
| 56 |  | Manual Switch Over during Ramp up | PCP-A | PCP-B
| 57 |  | Manual Switch Over during Ramp up | PCP-B | PCP-A
| 58 |  | Verify | Continuous Steady Operation
| 59 |  |  | Ramping Done and Holding the target Value
| 60 |  |  | No Transients, no unexpectd Time Delay
| 61 |  | Order STOP Ramping while ramping
| 62 |  | Verify | Ramping Stopped smoothly
| 63 |  |  | No Transients, no unexpected Time Delay
| 64 |  | Ramp Up | from stopped value | 500 Amps | 100 A/Min
| 65 |  | Order transfer to Power Control while ramping
| 66 |  | Verify | No transfer to power control
| 67 |  |  | No transient change in DC current
| 68 |  |  | Continuous Steady Operation
| 69 |  |  | Ramping Done and Holding the target Value
| 70 |  |  | No Transients, no unexpectd Time Delay
| 71 |  | Ramp Down | 500 Amps | 303 Amps | 100 A/Min
| 72 |  | Verify | Continuous Steady Operation
| 73 |  |  | Ramping Done and Holding the target Value
| 74 |  |  | No Transients, no unexpected Time Delay
Test Acceptance Criteria | 75 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 76 |  | All Operations executed successfully
| 77 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 78 |  | All thyristor check-back signals are available.
| 79 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 80 |  | Measuring quantities are available and the values are within the specified range and phase.
| 81 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 82 |  | No Stuck Condition
| 83 |  | No False Tripping by DC Protection System
| 84 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 85 |  | No Tripping in AC side of converter Station
k

## Reduced V Operations, P
Monopole Low Power Tests
8-Normal/Reduced Voltage Operation Joint Power Control, Ground return
Test Objective | The test objective is to check control system perfo rmance under reduced voltage operation mode.
Condition | Sr. No. | Station | Action | Equipment/Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side switchyard status | During Pole-I testing
| 4 |  | See Status Table "P1-GR" |  |  | Ground Return Mode
| 5 |  | See Status Table "Mat-P2-ISOLAT" for Matiari and "Lah-P2-ISOLAT" for Lahore. |  |  | Isolation Mode
| 6 |  | During Pole-II testing
| 7 |  | See Status Table "Mat-P1-ISOLAT" for Matiari and "Lah-P1-ISOLAT" for Lahore. |  |  | Isolation Mode
| 8 |  | See Status Table "P2-GR" |  |  | Ground Return Mode
| 9 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 10 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 11 |  | All electrical connections are available.
| 12 |  | Correct grounding of all equipment is available.
| 13 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 14 |  | Thyristor valves and valve hall is cleaned.
| 15 |  | Verify Sequence of Events Recorder (SER) and make sure that no relevant alarms are present, and all systems are operational.
Inter-station telecommunication check of control and protection signals
| 17 |  | Converter valve low voltage tests must be completed.
| 18 |  | Air humidity and temperature in valve hall are within expected limits.
| 19 |  | Normal Operation, Separate Current Control without Telecom with Ground Return Mode (Annex-C-7 must be successful)
| 20 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (400 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 21 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 22 |  | Return | Ground |  | Ground Return Mode
| 23 |  | Udc Mode | Reduced |  | ±462kV
| 24 |  | Telecom Mode | Operational
| 25 |  | Master Station | Matiari
| 26 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 27 |  |  | B | Standby
| 28 |  | Pole Control Protection (PCP) | A | ACTIVE
| 29 |  |  | B | Standby
| 30 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 31 |  | Station Control Mode | Joint | ACTIVE | Matiari & Lahore will operate jointly.
| 32 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 33 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Manual/Protection Triggering Reduced Voltage | 34 | Matiari | Make sure Voltages are set in reduced Voltage mode, 80% (528kV)
| 35 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 36 | Matiari & Lahore | Start the Pole, | Power | 200MW
| 37 |  |  | Ramp Rate: | 50 MW/Min
| 38 |  | Wait to achieve Target Value | Max Time | 5 min
| 39 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 40 |  |  | DC Voltages | 528 kV
| 41 |  |  | RPC Operation | BP-11/13 , HP24/36
| 42 | Lahore |  | Extinction Angle (g) | 17°
| 43 |  |  | DC Voltages | Range to be mentioned
| 44 |  |  | RPC Operation | 1xHP12/24
| 45 | Matiari/Lahore | Verify | Normal start at 80% reduced voltage with minimum power (DC current of 379A)
| 46 |  |  | Stable Operation
| 47 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 48 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 49 | Lahore |  | 1xHP12/24
| 50 | Matiari | Set manually reduced Voltage mode 70%
| 51 | Matiari/ Lahore | Verify | DC voltage ramps down to 70% (462kV)
| 52 |  |  | DC power remains constant
| 53 |  |  | DC current ramps up to 433A
| 54 |  |  | No transients
| 55 | Matiari | Order Normal Voltages (660kV)
| 56 |  | Verify | DC Voltage is ramping up to Normal Voltage (660kV)
| 57 |  |  | DC power remains constant
| 58 |  |  | DC current ramps down to 303A
| 59 |  |  | No transients
| 60 |  | Stop the Pole
| 61 | Matiari/Lahore | Verify Performance parameters | Retard, Reduced Current
| 62 |  |  | Firing angle (α) | 90°
| 63 | Lahore | Initiate the sequence of MASTER station.
| 64 |  | Order Reduced Voltages (70%/470kV)
| 65 |  | Start the Pole, | Power | 200MW
| 66 |  |  | Ramp Rate: | 100 MW/Min
| 67 |  | Wait to achieve Target Value | Max Time | 5 min
| 68 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 69 |  |  | DC Voltages | 470 kV
| 70 |  |  | RPC Operation | BP-11/13 , HP24/36
| 71 | Lahore |  | Extinction Angle (g) | 17°
| 72 |  |  | DC Voltages | Range to be mentioned
| 73 |  |  | RPC Operation | 1xHP12/24
| 74 | Matiari/Lahore | Verify | Normal start at 70% reduced voltage with minimum power (DC current of 433A)
| 75 |  |  | Stable Operation
| 76 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 77 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 78 | Lahore |  | 1xHP12/24
| 79 | Lahore | Order Normal Voltages (660kV)
| 80 |  | Verify | DC Voltage is ramping up to Normal Voltage (660kV)
| 81 |  |  | DC power remains constant
| 82 |  |  | DC current ramps down to 303A
| 83 |  |  | No transients
Manual/Protection Triggering Reduced Voltage | 84 | Matiari | Initiate Sequence of Master Station
| 85 |  | Set manually reduced Voltage mode 70%
| 86 |  | Verify | DC voltage ramps down to 70% (462kV)
| 87 |  |  | DC power remains constant
| 88 |  |  | DC current ramps up to 433A
| 89 |  |  | No transients
| 90 |  | Order Normal Voltages (660kV)
| 91 |  | Verify | DC Voltage is ramping up to Normal Voltage (660kV)
| 92 |  |  | DC power remains constant
| 93 |  |  | DC current ramps down to 303A
| 94 |  |  | No transients
| 95 | Lahore | Initiate Sequence of Master Station
| 96 |  | Set manually reduced Voltage mode 70%
| 97 |  | Verify | DC voltage ramps down to 70% (462kV)
| 98 |  |  | DC power remains constant
| 99 |  |  | DC current ramps up to 433A
| 100 |  |  | No transients
| 101 |  | Order Normal Voltages (660kV)
| 102 |  | Verify | DC Voltage is ramping up to Normal Voltage (660kV)
| 103 |  |  | DC power remains constant
| 104 |  |  | DC current ramps down to 303A
| 105 |  |  | No transients
| 106 | Matiari | Initiate Sequence of Master Station
| 107 | Matiari/ Lahore | Instruct Test Commander to Set REDUCED VOLTAGE from the DC-line Protection (70% of nominal voltage)
| 108 |  | Verify | Sharp reduction in DC votlage to 70% (462kV)
| 109 |  |  | DC power remains unchanged
| 110 |  | Instruct Test Commander to change the modified settings back to default.
| 111 |  | Disabled the telecommunication in both channels .
| 112 |  | Verify | No disturbances in the power transmission.
| 113 |  |  | Voltage remained steady at REDUCED VOLTAGE level.
| 114 |  | Enabled the telecommunication in both channels . Again
| 115 | Lahore | Initiate the sequence of MASTER station.
| 116 |  | Order Normal Voltage
| 117 |  | Verify | Smooth voltage ramp to 660kV
| 118 |  |  | No change in dc power
| 119 |  | Stop the Pole
Power / Current Ramp | 120 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions. |  |  | If pole is being operated at 200 MW ignore this step
| 121 | Matiari | Start the Pole, | Power | 200MW
| 122 |  |  | Ramp Rate: | 50 MW/Min
| 123 |  | Wait to achieve Target Value | Max Time | 5 min
| 124 |  | Set manually REDUCED VOLTAGE mode (70% of nominal voltage).
| 125 |  | Ramp Up | 200 MW | 400 MW | 50 MW/Min
| 126 |  | Order TRANSFER TO Current CONTROL while ramping
| 127 | Matiari / Lahore | Verify | no transfer during the power ramping
| 128 |  |  | no transient change in power
| 129 |  |  | No disturbances in the power transmission.
| 130 |  |  | Voltage remained steady at REDUCED VOLTAGE level.
| 131 | Matiari | Order Normal Voltages (660kV)
| 132 |  | Manual Switch Over during voltage ramp | PCP-A to | PCP-B
| 133 |  | Manual Switch Over during voltage ramp | PCP-B to | PCP-A
| 134 | Lahore | Initiate the sequence of MASTER station.
| 135 |  | Set manually REDUCED VOLTAGE mode (70% of nominal voltage).
| 136 |  | Ramp Down | 400 MW | 200 MW | 50 MW/Min
| 137 | Matiari / Lahore | Verify | No disturbances in the power transmission.
| 138 |  |  | Voltage remained steady at REDUCED VOLTAGE level.
| 139 | Lahore | Order Normal Voltages (660kV)
| 140 |  | Manual Switch Over during voltage ramp | PCP-A to | PCP-B
| 141 |  | Manual Switch Over during voltage ramp | PCP-B to | PCP-A
Test Acceptance Criteria | 142 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 143 |  | All Operations executed successfully
| 144 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 145 |  | All thyristor check-back signals are available.
| 146 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 147 |  | Measuring quantities are available and the values are within the specified range and phase.
| 148 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 149 |  | No Stuck Condition
| 150 |  | No False Tripping by DC Protection System
| 151 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 152 |  | No Tripping in AC side of converter Station

## RPC
Monopole Low Power Tests
9-Reactive Power Control Joint Power Control, Ground return
Test Objective | The test objective is to check reactive power and AC voltage control performance of DC system.
Condition | Sr. No. | Station | Action | Equipment/Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side switchyard status | During Pole-I testing
| 4 |  | See Status Table "P1-GR" |  |  | Ground Return Mode
| 5 |  | See Status Table "Mat-P2-ISOLAT" for Matiari and "Lah-P2-ISOLAT" for Lahore. |  |  | Isolation Mode
| 6 |  | During Pole-II testing
| 7 |  | See Status Table "Mat-P1-ISOLAT" for Matiari and "Lah-P1-ISOLAT" for Lahore. |  |  | Isolation Mode
| 8 |  | See Status Table "P2-GR" |  |  | Ground Return Mode
| 9 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 10 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 11 |  | All electrical connections are available.
| 12 |  | Correct grounding of all equipment is available.
| 13 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 14 |  | Thyristor valves and valve hall is cleaned.
| 15 |  | Verify Sequence of Events Recorder (SER) and make sure that no relevant alarms are present, and all systems are operational.
Inter-station telecommunication check of control and protection signals
| 17 |  | Converter valve low voltage tests must be completed.
| 18 |  | Air humidity and temperature in valve hall are within expected limits.
| 19 |  | Steady State Operation Tests (Power Control Mode) in Normal Power Direction with Ground Return Mode (Annex-C-6 have been successful)
| 20 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (750 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 21 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 22 |  | Return | Ground |  | Ground Return Mode
| 23 |  | Udc Mode | Normal |  | ±660kV
| 24 |  | Telecom Mode | Operational
| 25 |  | Master Station | Matiari
| 26 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 27 |  |  | B | Standby
| 28 |  | Pole Control Protection (PCP) | A | ACTIVE
| 29 |  |  | B | Standby
| 30 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 31 |  | Station Control Mode | Joint | ACTIVE | Matiari & Lahore will operate jointly.
| 32 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 33 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Filter Requirement Test | 34 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 35 | Matiari & Lahore | Start the Pole | Power | 200 MW
| 36 |  |  | Ramp Rate: | 50 MW/Min
| 37 |  | Wait to achieve Target Value | Max Time | 5 min
| 38 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 39 |  |  | DC Voltages | 660kV
| 40 |  |  | RPC Operation | BP-11/13 , HP24/36
| 41 | Lahore |  | Extinction Angle (g) | 17°
| 42 |  |  | DC Voltages | Range to be mentioned
| 43 |  |  | RPC Operation | 1xHP12/24
| 44 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 45 | Lahore |  | 1xHP12/24
| 46 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 550 MW with DC System. (Sudden load sharing from AC corridor to DC corridor will happen in next step)
| 47 | Matiari | Ramp Up | 200 MW | 750 MW | 50 MW/Min
| 48 | Matiari | Verify RPC action | No additional filters
| 49 | Lahore |  | No additional filters
| 50 | AC Network | NPCC makes sure, parallel AC corridor has margin for sharing 550 MW with DC System. (Sudden load sharing from AC corridor to DC corridor will happen in next step)
| 51 | Matiari | Ramp Down | 750 MW | 200 MW | 50 MW/Min
Filter Replacement Test | 52 | Matiari | Start the Pole | Power | 200 MW | If pole is already been operated at 200 MW ignore this step
| 53 |  |  | Ramp Rate: | 50MW/min
| 54 |  | Wait to achieve Target Value | Max Time | 5 min
| 55 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 56 |  |  | DC Voltages | 660kV
| 57 |  |  | RPC Operation | BP-11/13 , HP24/36
| 58 | Lahore |  | Extinction Angle (g) | 17°
| 59 |  |  | DC Voltages | Range to be mentioned
| 60 |  |  | RPC Operation | 1xHP12/24
| 61 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 62 | Lahore |  | 1xHP12/24
| 63 | Matiari | Order RPC from Automatic to Manual
| 64 |  | Switch off connected sub-bank BP-11/13
| 65 |  | Verify that another BP-11/13 got connected within 1 second
| 66 |  | Switch off connected sub-bank HP-24/36
| 67 |  | Verify that another HP-24/36 got connected within 1 second
| 68 | Lahore | Switch off connected sub-bank HP-12/24
| 69 |  | Verify that another HP-12/24 got connected within 1 second
| 70 | Matiari | Order RPC from Manual to Automatic
Reactive Power Control | 71 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions. |  |  | If pole is already been operated at 200 MW ignore this step
| 72 | Matiari & Lahore | Start the Pole | Power | 200 MW
| 73 |  |  | Ramp Rate: | 50 MW/Min
| 74 |  | Wait to achieve Target Value | Max Time | 5 min
| 75 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 76 |  |  | DC Voltages | 660kV
| 77 |  |  | RPC Operation | BP-11/13 , HP24/36
| 78 | Lahore |  | Extinction Angle (g) | 17°
| 79 |  |  | DC Voltages | Range to be mentioned
| 80 |  |  | RPC Operation | 1xHP12/24
| 81 | Matiari | Verify Q-Control action | BP-11/13, HP-24/36
| 82 | Lahore |  | 1xHP-12/24
| 83 | Matiari | Ramp Up | 200 MW | 400 MW | 50 MW/Min
| 84 | Matiari | Verify Q-Control action | No additional filter
| 85 | Lahore |  | 1 additional HP12/24
| 86 | Lahore | Instruct Test Commander to change the Q-reference (Q-reference should subject to the prevailing situation) in order to provoke a filter switching ON by the RPC.
| 87 |  | Verify that an AC filter is switched ON accordingly.
| 88 |  | Restore the Q-reference,
Voltage Control | 89 | Matiari/Lahore C/S DC side | Verify U-Control instead of Q-Control.
| 90 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions. |  |  | If pole is already been operated at 200 MW ignore this step
| 91 | Matiari & Lahore | Start the Pole | Current | 200 MW
| 92 |  |  | Ramp Rate: | 50 MW/Min
| 93 |  | Wait to achieve Target Value | Max Time | 5 min
| 94 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 95 |  |  | DC Voltages | 660kV
| 96 |  |  | RPC Operation | BP-11/13 , HP24/36
| 97 | Lahore |  | Extinction Angle (g) | 17°
| 98 |  |  | DC Voltages | Range to be mentioned
| 99 |  |  | RPC Operation | 1xHP12/24
| 100 | Matiari | Verify U-Control action | BP-11/13, HP-24/36
| 101 | Lahore |  | 1xHP-12/24
| 102 | Matiari | Ramp Up | 200 MW | 400 MW | 50 MW/Min
| 103 | Matiari | Instruct Test Commander to change the U-reference (U-reference should subject to the prevailing situation) in order to provoke a filter switching ON by the RPC.
| 104 |  | Verify that an AC filter is switched ON accordingly.
| 105 |  | Restore the U-reference,
Umax Control | 106 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions. |  |  | If pole is already been operated at 200 MW ignore this step
| 107 | Matiari & Lahore | Start the Pole | Current | 200 MW
| 108 |  |  | Ramp Rate: | 50 MW/Min
| 109 |  | Wait to achieve Target Value | Max Time | 5 min
| 110 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 111 |  |  | DC Voltages | 660kV
| 112 |  |  | RPC Operation | BP-11/13 , HP24/36
| 113 | Lahore |  | Extinction Angle (g) | 17°
| 114 |  |  | DC Voltages | Range to be mentioned
| 115 |  |  | RPC Operation | 1xHP12/24
| 116 | Matiari | Verify U-Control action | BP-11/13, HP-24/36
| 117 | Lahore |  | 1xHP-12/24
| 118 | Matiari | Ramp Up | 200 MW | 400 MW | 50 MW/Min
| 119 | Matiari | Decrease the Umax upper limit value to a value which is lower than AC voltage.
| 120 |  | Instruct Test commander to change the U-reference in order to provoke a filter switching ON by the RPC.
| 121 |  | Verify that there is no more input filter in Matiari station because of Umax limit.
| 122 |  | Increase the Umax upper limit value to a value which is higher than AC voltage.
| 123 |  | Verify that one sub bank BP11/13 in Matiari station switching on.
| 124 |  | Restore the Umax upper limit value and U-reference to the initial setting value.
| 125 | Lahore | Decrease the Umax upper limit value to a value which is lower than AC voltage.
| 126 |  | Instruct Test commander to change the U-reference in order to provoke a filter switching ON by the RPC.
| 127 |  | Verify that there is no more input filter in Lahore station because of Umax limit.
| 128 |  | Increase the Umax upper limit value to a value which is higher than AC voltage.
| 129 |  | Verify that one sub bank HP12/24 in Lahore station switching on.
| 130 |  | Restore the Umax upper limit value and U-reference to the initial setting value.
Test Acceptance Criteria | 131 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 132 |  | All Operations executed successfully
| 133 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 134 |  | All thyristor check-back signals are available.
| 135 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 136 |  | Measuring quantities are available and the values are within the specified range and phase.
| 137 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 138 |  | No Stuck Condition
| 139 |  | No False Tripping by DC Protection System
| 140 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 141 |  | No Tripping in AC side of converter Station
kkkk

## GRMR
Monopole Low Power Tests
10-Ground/Metallic Return Transfer Joint Current Control, Ground return
Test Objective | The test objective is to check transfer sequence of Ground/Metallic Return configuration.
Condition | Sr. No. | Station | Action | Equipment/Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side switchyard status | During Pole-I testing
| 4 |  | See Status Table "P1-GR" |  |  | Ground Return Mode
| 5 |  | See Status Table "Mat-P2-ISOLAT" for Matiari and "Lah-P2-ISOLAT" for Lahore. |  |  | Isolation Mode
| 6 |  | During Pole-II testing
| 7 |  | See Status Table "Mat-P1-ISOLAT" for Matiari and "Lah-P1-ISOLAT" for Lahore. |  |  | Isolation Mode
| 8 |  | See Status Table "P2-GR" |  |  | Ground Return Mode
| 9 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 10 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 11 |  | All electrical connections are available.
| 12 |  | Correct grounding of all equipment is available.
| 13 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 14 |  | Thyristor valves and valve hall is cleaned.
| 15 |  | Verify Sequence of Events Recorder (SER) and make sure that no relevant alarms are present, and all systems are operational.
Inter-station telecommunication check of control and protection signals
| 17 |  | Converter valve low voltage tests must be completed.
| 18 |  | Air humidity and temperature in valve hall are within expected limits.
| 19 |  | Steady State Operation Tests (Power Control Mode) in Normal Power Direction with Ground Return Mode (Annex-C-6 have must be successful)
| 20 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (200 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 21 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 22 |  | Return | Ground |  | Ground Return Mode
| 23 |  | Udc Mode | Normal |  | ±660kV
| 24 |  | Telecom Mode | Operational
| 25 |  | Master Station | Matiari
| 26 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 27 |  |  | B | Standby
| 28 |  | Pole Control Protection (PCP) | A | ACTIVE
| 29 |  |  | B | Standby
| 30 |  | Transmission Control Mode | Current | ACTIVE | HVDC will operate in current control mode.
| 31 |  | Station Control Mode | Joint | ACTIVE | Matiari & Lahore will operate jointly.
| 32 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 33 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Ground/Metallic Return Transfer | 34 | Matiari/Lahore C/S DC side | Verify that the other pole is isolated and both stations are ready for metallic return operation.
| 35 |  | Verify Ready for Operation Conditions.
| 36 | Matiari & Lahore | Start the Pole, | Current | 303 Amps
| 37 |  |  | Ramp Rate: | 100 A/Min
| 38 |  | Wait to achieve Target Value | Max Time | 5 min
| 39 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 40 |  |  | DC Voltages | 660kV
| 41 |  |  | RPC Operation | BP-11/13 , HP24/36
| 42 | Lahore |  | Extinction Angle (g) | 17°
| 43 |  |  | DC Voltages | Range to be mentioned
| 44 |  |  | RPC Operation | 1xHP12/24
| 45 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 46 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 47 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 48 | Lahore |  | 1xHP12/24
| 49 | Matiari/Lahore | Order TRANSFER TO METALLIC RETURN.
| 50 | Matiari/Lahore | Verify | Correct sequential operation of switches and breakers.
| 51 |  |  | Correct operation of MRTB in Matiari (The operation of the breaker should be visually observed carefully in case that the sequence is interrupted by maloperation)
| 52 |  |  | No disturbance in power transfer.
| 53 |  |  | Check whether all related switches and breakers in Matiari and LAHORE are correctly operated in line with the technical specification.
| 54 | Matiari/Lahore | Order TRANSFER TO GROUND RETURN.
| 55 | Matiari/Lahore | Verify | Correct sequential operation of switches and breakers.
| 56 |  |  | Correct operation of GRTS in Matiari (The operation of the breaker should be visually observed carefully in case that the sequence is interrupted by maloperation)
| 57 |  |  | No disturbance in power transfer.
| 58 |  |  | Check whether all related switches and breakers in Matiari and LAHORE are correctly operated in line with the technical specification.
| 59 | Matiari/Lahore | Order TRANSFER TO METALLIC RETURN. During GR→MR, Initiate a manual switchover from PCPA to PCPB, and then from PCPB to PCPA in Matiari station.
| 60 | Matiari | Verify | Correct sequential operation of switches and breakers.
| 61 |  |  | Correct operation of MRTB in Matiari (The operation of the breaker should be visually observed carefully in case that the sequence is interrupted by maloperation)
| 62 |  |  | System GR/MR transfer Normally and no transient changes in DC current in Matiari.
| 63 |  |  | No disturbance in power transfer.
| 64 |  |  | Check whether all related switches and breakers in Matiari and LAHORE are correctly operated in line with the technical specification.
| 65 | Matiari/Lahore | Order TRANSFER TO GROUND RETURN.
| 66 | Lahore | Verify | Correct sequential operation of switches and breakers.
| 67 |  |  | Correct operation of MRTB in Matiari (The operation of the breaker should be visually observed carefully in case that the sequence is interrupted by maloperation)
| 68 |  |  | System GR/MR transfer Normally and no transient changes in DC current in Matiari.
| 69 |  |  | No disturbance in power transfer.
| 70 |  |  | Check whether all related switches and breakers in Matiari and LAHORE are correctly operated in line with the technical specification.
Metallic Return Operation with Station Ground at Lahore C/s | 71 | Matiari/Lahore | Order TRANSFER TO METALLIC RETURN.
| 72 | Matiari & Lahore | Start the Pole, | Current | 303 Amps
| 73 |  |  | Ramp Rate: | 100 A/Min
| 74 |  | Wait to achieve Target Value | Max Time | 5 min
| 75 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 76 |  |  | DC Voltages | 660kV
| 77 |  |  | RPC Operation | BP-11/13 , HP24/36
| 78 | Lahore |  | Extinction Angle (g) | 17°
| 79 |  |  | DC Voltages | Range to be mentioned
| 80 |  |  | RPC Operation | 1xHP12/24
| 81 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 82 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 83 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 84 | Lahore |  | 1xHP12/24
| 85 | Matiari/Lahore | Instruct Test Commander to Simulate Electrode Line Open Circuit Protection Zone I Action by executing the following action, and then the NBGS would be automatically closed in LAHORE
| 86 | Lahore | Then the NBGS would be automatically closed in LAHORE
| 87 | Matiari/Lahore | Order OPEN (WN3Q11) manually
| 88 | Matiari | Stop the Pole
| 89 |  | Verify Performance parameters | Retard, Reduced Current
| 90 | Lahore |  | Firing angle | 90
| 91 |  | Verify DC system is in metallic return mode and LAHORE station operates with station ground
| 92 | Matiari | Start the Pole | Current | 303 Amps
| 93 |  |  | Ramp Rate: | 100 A/Min
| 94 |  | Wait to achieve Target Value | Max Time | 5 min
| 95 |  | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 96 |  |  | DC Voltages | 660kV
| 97 |  |  | RPC Operation | BP-11/13 , HP24/36
| 98 | Lahore |  | Extinction Angle (g) | 17°
| 99 |  |  | DC Voltages | Range to be mentioned
| 100 |  |  | RPC Operation | 1xHP12/24
| 101 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 102 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 103 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 104 | Lahore |  | 1xHP12/24
| 105 | Matiari | Stop the Pole
| 106 |  | Verify Performance parameters | Retard, Reduced Current
| 107 | Lahore |  | Firing angle | 90
| 108 | Matiari/Lahore | Restore Settings
| 109 |  | Order Close WN3Q11 and then Open NBGS.
Test Acceptance Criteria | 110 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 111 |  | All Operations executed successfully
| 112 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 113 |  | All thyristor check-back signals are available.
| 114 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 115 |  | Measuring quantities are available and the values are within the specified range and phase.
| 116 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 117 |  | No Stuck Condition
| 118 |  | No False Tripping by DC Protection System
| 119 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 120 |  | No Tripping in AC side of converter Station

## BackUp Control
Monopole Low Power Tests
11-Backup Control Joint Power Control, Ground return
Test Objective | The test objective is to check control system perfo rmance under reduced voltage operation mode.
Condition | Sr. No. | Station | Action | Equipment/Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side switchyard status | During Pole-I testing
| 4 |  | See Status Table "P1-GR" |  |  | Ground Return Mode
| 5 |  | See Status Table "Mat-P2-ISOLAT" for Matiari and "Lah-P2-ISOLAT" for Lahore. |  |  | Isolation Mode
| 6 |  | During Pole-II testing
| 7 |  | See Status Table "Mat-P1-ISOLAT" for Matiari and "Lah-P1-ISOLAT" for Lahore. |  |  | Isolation Mode
| 8 |  | See Status Table "P2-GR" |  |  | Ground Return Mode
| 9 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 10 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 11 |  | All electrical connections are available.
| 12 |  | Correct grounding of all equipment is available.
| 13 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 14 |  | Thyristor valves and valve hall is cleaned.
| 15 |  | Verify Sequence of Events Recorder (SER) and make sure that no relevant alarms are present, and all systems are operational.
Inter-station telecommunication check of control and protection signals
| 17 |  | Converter valve low voltage tests must be completed.
| 18 |  | Air humidity and temperature in valve hall are within expected limits.
| 19 |  | Set tap changer to position giving lowest valve voltage
| 20 |  | Steady State Operation Tests (Power Control Mode) in Normal Power Direction with Ground Return Mode (Annex-C-6 must be successful)
| 21 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (400 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 22 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 23 |  | Return | Ground |  | Ground Return Mode
| 24 |  | Udc Mode | Normal |  | ±660 kV
| 25 |  | Telecom Mode | Operational
| 26 |  | Master Station | Matiari
| 27 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 28 |  |  | B | Standby
| 29 |  | Pole Control Protection (PCP) | A | ACTIVE
| 30 |  |  | B | Standby
| 31 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 32 |  | Station Control Mode | Joint | ACTIVE | Matiari & Lahore will operate jointly.
| 33 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 34 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Monopole Start/Stop in Backup Panel | 35 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 36 |  | Switch DC Local Control Interface from ‘REMOTE’ to ‘LOCAL’.
| 37 | Matiari & Lahore | Start the Pole, | Current | 200 MW
| 38 |  |  | Ramp Rate: | 50 MW/Min
| 39 |  | Wait to achieve Target Value | Max Time | 5 min
| 40 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 41 |  |  | DC Voltages | 660kV
| 42 |  |  | RPC Operation | BP-11/13 , HP24/36
| 43 | Lahore |  | Extinction Angle (g) | 17°
| 44 |  |  | DC Voltages | Range to be mentioned
| 45 |  |  | RPC Operation | 1xHP12/24
| 46 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 47 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 48 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 49 | Lahore |  | 1xHP12/24
| 50 | Matiari/Lahore | Stop the Pole
| 51 |  | Verify Performance parameters | Retard, Reduced Current
| 52 | Lahore |  | Firing angle (α) | 90°
Monopole Ramp up/down in Backup Panel | 53 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 54 |  | Switch DC Local Control Interface from ‘REMOTE’ to ‘LOCAL’.
| 55 | Matiari & Lahore | Start the Pole, | Power | 200 MW
| 56 |  |  | Ramp Rate: | 50 MW/Min
| 57 |  | Wait to achieve Target Value | Max Time | 5 min
| 58 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 59 |  |  | DC Voltages | 660kV
| 60 |  |  | RPC Operation | BP-11/13 , HP24/36
| 61 | Lahore |  | Extinction Angle (g) | 17°
| 62 |  |  | DC Voltages | Range to be mentioned
| 63 |  |  | RPC Operation | 1xHP12/24
| 64 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 65 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 66 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 67 | Lahore |  | 1xHP12/24
| 68 | Matiari | Ramp Up | 200 MW | 400 MW | 50 MW/Min
| 69 |  | Order STOP RAMPING.
| 70 |  | Verify also that the ramp could stop while ramping
| 71 |  | Ramp Up | from stopped value | 400MW | 50 MW/Min
| 72 |  | Verify that the current reaches the reference value after each ramping is completed in both stations and that the ramping process is smooth and without disturbances.
| 73 | Lahore | Initiate the sequence of MASTER station.
| 74 |  | Ramp Down | 400 MW | 200 MW | 50 MW/Min
| 75 |  | Order STOP RAMPING.
| 76 |  | Verify also that the ramp could stop while ramping
| 77 |  | Ramp Down | from stopped value | 200MW | 50 MW/Min
| 78 |  | Verify that the current reaches the reference value after each ramping is completed in both stations and that the ramping process is smooth and without disturbances.
| 79 |  | Switch DC Local Control Interface from ‘LOCAL’ to 'REMOTE'.
| 80 | Matiari/Lahore | Stop the Pole
| 81 |  | Verify Performance parameters | Retard, Reduced Current
| 82 | Lahore |  | Firing angle (α) | 90°
Test Acceptance Criteria | 83 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 84 |  | All Operations executed successfully
| 85 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 86 |  | All thyristor check-back signals are available.
| 87 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 88 |  | Measuring quantities are available and the values are within the specified range and phase.
| 89 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 90 |  | No Stuck Condition
| 91 |  | No False Tripping by DC Protection System
| 92 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 93 |  | No Tripping in AC side of converter Station
kkkk

## IOT GR Rev
Monopole Low Power Tests
12-Initial Operation Tests, Ground Return Operation, Reversed Power Direction Joint Current Control
Test Objective | Verify the basic function of deblock/block, manually switchover of control and protection system.
Condition | Sr. No. | Station | Action | Equipment/Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side switchyard status | During Pole-I testing
| 4 |  | See Status Table "P1-GR" |  |  | Ground Return Mode
| 5 |  | See Status Table "Mat-P2-ISOLAT" for Matiari and "Lah-P2-ISOLAT" for Lahore. |  |  | Isolation Mode
| 6 |  | During Pole-II testing
| 7 |  | See Status Table "Mat-P1-ISOLAT" for Matiari and "Lah-P1-ISOLAT" for Lahore. |  |  | Isolation Mode
| 8 |  | See Status Table "P2-GR" |  |  | Ground Return Mode
| 9 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 10 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 11 |  | All electrical connections are available.
| 12 |  | Correct grounding of all equipment is available.
| 13 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 14 |  | Thyristor valves and valve hall is cleaned.
| 15 |  | Verify Sequence of Events Recorder (SER) and make sure that no relevant alarms are present, and all systems are operational.
Inter-station telecommunication check of control and protection signals
| 17 |  | Converter valve low voltage tests must be completed.
| 18 |  | Air humidity and temperature in valve hall are within expected limits.
| 19 |  | All DC Low Power Tests as in Annex-C-1 to 11 must be successful
| 20 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (200 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 21 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Reverse |  | Lahore to Matiari
| 22 |  | Return | Ground |  | Ground Return Mode
| 23 |  | Udc Mode | Normal |  | ±660kV
| 24 |  | Telecom Mode | Operational
| 25 |  | Master Station | Lahore
| 26 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 27 |  |  | B | Standby
| 28 |  | Pole Control Protection (PCP) | A | ACTIVE
| 29 |  |  | B | Standby
| 30 |  | Transmission Control Mode | Current | ACTIVE | HVDC will operate in current control mode.
| 31 |  | Station Control Mode | Joint | ACTIVE | Matiari & Lahore will operate jointly.
| 32 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 33 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Pole Start/Stop Pole | 34 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 35 | Lahore | Start the Pole | Current | 303 A [200 MW]
| 36 |  |  | Ramp Rate: | 100A/Min
| 37 |  | Wait to achieve Target Value | Max Time | 5 min
| 38 |  | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 39 |  |  | DC Voltages | 660kV
| 40 |  |  | RPC Operation | BP-11/13 , HP24/36
| 41 | Matiari |  | Extinction Angle (g) | 17°
| 42 |  |  | DC Voltages | Range to be mentioned
| 43 |  |  | RPC Operation | 1xHP12/24
| 44 | Matiari/Lahore | Verify stable operation at minimum current.
| 45 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 46 | Matiari | Verify RPC action | BP-11/13 , HP24/36
| 47 | Lahore |  | 1xHP12/24
| 48 | Lahore | Stop the Pole
| 49 |  | Verify Performance parameters | Retard, Reduced Current
| 50 | Matiari |  | Firing angle (α) | 90°
Control System Switchover | 51 | Lahore | Verify Ready for Operation Conditions. |  |  | If pole is already been operated at 200 MW ignore this step
| 52 |  | Start the Pole | Current | 303 A [200 MW]
| 53 |  |  | Ramp Rate: | 100A/Min
| 54 |  | Verify | PCP-A | ACTIVE
| 55 |  | Switch Control System | PCP-A to | PCP-B
| 56 |  | Verify | Continuous Steady Operation of the transmission
| 57 |  |  | PCP-B is active
| 58 |  |  | No Transients
| 59 |  | Verify | SC-A | ACTIVE
| 60 |  | Switch Control System | SC-A to | SC-B
| 61 |  | Verify | Continuous Steady Operation of the transmission
| 62 |  |  | SC-B is active
| 63 |  |  | No Transients
| 64 |  | Switch Control System | PCP-B to | PCP-A
| 65 |  | Verify | Continuous Steady Operation of the transmission
| 66 |  |  | PCP-A is active
| 67 |  |  | No Transients
| 68 |  | Switch Control System | SC-B to | SC-A
| 69 |  | Verify | Continuous Steady Operation of the transmission
| 70 |  |  | SC-A is active
| 71 |  |  | No Transients
| 72 | Matiari | Verify | PCP-A | ACTIVE
| 73 |  | Switch Control System | PCP-A to | PCP-B
| 74 |  | Verify | Continuous Steady Operation of the transmission
| 75 |  |  | PCP-B is active
| 76 |  |  | No Transients
| 77 |  | Verify | SC-A | ACTIVE
| 78 |  | Switch Control System | SC-A to | SC-B
| 79 |  | Verify | Continuous Steady Operation of the transmission
| 80 |  |  | SC-B is active
| 81 |  |  | No Transients
| 82 |  | Switch Control System | PCP-B to | PCP-A
| 83 |  | Verify | Continuous Steady Operation of the transmission
| 84 |  |  | PCP-A is active
| 85 |  |  | No Transients
| 86 |  | Switch Control System | SC-B to | SC-A
| 87 |  | Verify | Continuous Steady Operation of the transmission
| 88 |  |  | SC-A is active
| 89 |  |  | No Transients
Ground/Metallic Return Transfer | 90 | Matiari/Lahore C/S DC side | Verify that the other pole is isolated and both stations are ready for metallic return operation.
| 91 |  | Verify Ready for Operation Conditions. |  |  | If pole is already been operated at 200 MW ignore this step
| 92 | Matiari & Lahore | Start the Pole, | Current | 303 Amps
| 93 |  |  | Ramp Rate: | 100 A/Min
| 94 |  | Wait to achieve Target Value | Max Time | 5 min
| 95 | Lahore | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 96 |  |  | DC Voltages | 660kV
| 97 |  |  | RPC Operation | BP-11/13 , HP24/36
| 98 | Matiari |  | Extinction Angle (g) | 17°
| 99 |  |  | DC Voltages | Range to be mentioned
| 100 |  |  | RPC Operation | 1xHP12/24
| 101 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 102 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 103 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 104 | Lahore |  | 1xHP12/24
| 105 | Matiari/Lahore | Order TRANSFER TO METALLIC RETURN.
| 106 | Matiari/Lahore | Verify | Correct sequential operation of switches and breakers.
| 107 |  |  | Correct operation of MRTB in Matiari (The operation of the breaker should be visually observed carefully in case that the sequence is interrupted by maloperation)
| 108 |  |  | No disturbance in power transfer.
| 109 |  |  | Check whether all related switches and breakers in Matiari and LAHORE are correctly operated in line with the technical specification.
| 110 | Matiari/Lahore | Order TRANSFER TO GROUND RETURN.
| 111 | Matiari/Lahore | Verify | Correct sequential operation of switches and breakers.
| 112 |  |  | Correct operation of GRTS in Matiari (The operation of the breaker should be visually observed carefully in case that the sequence is interrupted by maloperation)
| 113 |  |  | No disturbance in power transfer.
| 114 |  |  | Check whether all related switches and breakers in Matiari and LAHORE are correctly operated in line with the technical specification.
Test Acceptance Criteria | 115 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 116 |  | All Operations executed successfully
| 117 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 118 |  | All thyristor check-back signals are available.
| 119 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 120 |  | Measuring quantities are available and the values are within the specified range and phase.
| 121 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 122 |  | No Stuck Condition
| 123 |  | No False Tripping by DC Protection System
| 124 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 125 |  | No Tripping in AC side of converter Station
kkkk

## IOT MR Rev
Monopole Low Power Tests
13-Initial Operation Tests, Ground Return Operation, Reversed Power Direction Joint Power Control, Ground return
Test Objective | Verify the basic function of deblock/block, manually switchover of control and protection system.
Condition | Sr. No. | Station | Action | Equipment/Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side switchyard status | During Pole-I testing
| 4 |  | See Status Table "P1-GR" |  |  | Metalic Return Mode
| 5 |  | See Status Table "Mat-P2-ISOLAT" for Matiari and "Lah-P2-ISOLAT" for Lahore. |  |  | Isolation Mode
| 6 |  | During Pole-II testing
| 7 |  | See Status Table "Mat-P1-ISOLAT" for Matiari and "Lah-P1-ISOLAT" for Lahore. |  |  | Isolation Mode
| 8 |  | See Status Table "P2-GR" |  |  | Metallic Return Mode
| 9 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 10 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 11 |  | All electrical connections are available.
| 12 |  | Correct grounding of all equipment is available.
| 13 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 14 |  | Thyristor valves and valve hall is cleaned.
| 15 |  | Verify Sequence of Events Recorder (SER) and make sure that no relevant alarms are present, and all systems are operational.
Inter-station telecommunication check of control and protection signals
| 17 |  | Converter valve low voltage tests must be completed.
| 18 |  | Air humidity and temperature in valve hall are within expected limits.
| 19 |  | Initial Operation Tests (Reverse Power) in Ground Return Mode (Annex-C-12) were successful.
| 20 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (200 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 21 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Reverse |  | Lahore to Matiari
| 22 |  | Return | Metallic |  | Ground Return Mode
| 23 |  | Udc Mode | Normal |  | ±660kV
| 24 |  | Telecom Mode | Operational
| 25 |  | Master Station | Matiari
| 26 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 27 |  |  | B | Standby
| 28 |  | Pole Control Protection (PCP) | A | ACTIVE
| 29 |  |  | B | Standby
| 30 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 31 |  | Station Control Mode | Joint | ACTIVE | Matiari & Lahore will operate jointly.
| 32 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 33 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Start/Stop Pole | 34 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 35 |  | Make Sure that configuration is set in Metallic Return Mode
| 36 | Lahore | Start the Pole | Power | 200 MW
| 37 |  |  | Ramp Rate: | 50 MW/min
| 38 |  | Wait to achieve Target Value | Max Time | 5 min
| 39 |  | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 40 |  |  | DC Voltages | 660kV
| 41 |  |  | RPC Operation | BP-11/13 , HP24/36
| 42 | Matiari |  | Extinction Angle (g) | 17°
| 43 |  |  | DC Voltages | Range to be mentioned
| 44 |  |  | RPC Operation | 1xHP12/24
| 45 | Matiari/Lahore | Verify stable operation at minimum current.
| 46 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 47 | Matiari | Verify RPC action | BP-11/13 , HP24/36
| 48 | Lahore |  | 1xHP12/24
| 49 | Lahore | Stop the Pole
| 50 |  | Verify Performance parameters | Retard, Reduced Current
| 51 | Matiari |  | Firing angle (α) | 90°
Control System Switchover | 52 | Lahore | Verify Ready for Operation Conditions. |  |  | If pole is already been operated at 200 MW ignore this step
| 53 |  | Start the Pole | Power | 200 MW
| 54 |  |  | Ramp Rate: | 50 MW/min
| 55 |  | Verify | PCP-A | ACTIVE
| 56 |  | Switch Control System | PCP-A to | PCP-B
| 57 |  | Verify | Continuous Steady Operation of the transmission
| 58 |  |  | PCP-B is active
| 59 |  |  | No Transients
| 60 |  | Verify | SC-A | ACTIVE
| 61 |  | Switch Control System | SC-A to | SC-B
| 62 |  | Verify | Continuous Steady Operation of the transmission
| 63 |  |  | SC-B is active
| 64 |  |  | No Transients
| 65 |  | Switch Control System | PCP-B to | PCP-A
| 66 |  | Verify | Continuous Steady Operation of the transmission
| 67 |  |  | PCP-A is active
| 68 |  |  | No Transients
| 69 |  | Switch Control System | SC-B to | SC-A
| 70 |  | Verify | Continuous Steady Operation of the transmission
| 71 |  |  | SC-A is active
| 72 |  |  | No Transients
| 73 | Matiari | Verify | PCP-A | ACTIVE
| 74 |  | Switch Control System | PCP-A to | PCP-B
| 75 |  | Verify | Continuous Steady Operation of the transmission
| 76 |  |  | PCP-B is active
| 77 |  |  | No Transients
| 78 |  | Verify | SC-A | ACTIVE
| 79 |  | Switch Control System | SC-A to | SC-B
| 80 |  | Verify | Continuous Steady Operation of the transmission
| 81 |  |  | SC-B is active
| 82 |  |  | No Transients
| 83 |  | Switch Control System | PCP-B to | PCP-A
| 84 |  | Verify | Continuous Steady Operation of the transmission
| 85 |  |  | PCP-A is active
| 86 |  |  | No Transients
| 87 |  | Switch Control System | SC-B to | SC-A
| 88 |  | Verify | Continuous Steady Operation of the transmission
| 89 |  |  | SC-A is active
| 90 |  |  | No Transients
| 91 | Lahore | Stop the Pole
| 92 |  | Verify Performance parameters | Retard, Reduced Current
| 93 | Matiari |  | Firing angle (α) | 90°
Test Acceptance Criteria | 94 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 95 |  | All Operations executed successfully
| 96 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 97 |  | All thyristor check-back signals are available.
| 98 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 99 |  | Measuring quantities are available and the values are within the specified range and phase.
| 100 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 101 |  | No Stuck Condition
| 102 |  | No False Tripping by DC Protection System
| 103 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 104 |  | No Tripping in AC side of converter Station
kkkk

## Disturbance
Monopole Low Power Tests
14-Disturbances Joint Power Control, Ground return
Test Objective | The test objective is to check control system perfo rmance under reduced voltage operation mode.
Condition | Sr. No. | Station | Action | Equipment/Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side switchyard status | During Pole-I testing
| 4 |  | See Status Table "P1-GR" |  |  | Ground Return Mode
| 5 |  | See Status Table "Mat-P2-ISOLAT" for Matiari and "Lah-P2-ISOLAT" for Lahore. |  |  | Isolation Mode
| 6 |  | During Pole-II testing
| 7 |  | See Status Table "Mat-P1-ISOLAT" for Matiari and "Lah-P1-ISOLAT" for Lahore. |  |  | Isolation Mode
| 8 |  | See Status Table "P2-GR" |  |  | Ground Return Mode
| 9 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 10 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 11 |  | All electrical connections are available.
| 12 |  | Correct grounding of all equipment is available.
| 13 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 14 |  | Thyristor valves and valve hall is cleaned.
| 15 |  | Verify Sequence of Events Recorder (SER) and make sure that no relevant alarms are present, and all systems are operational.
Inter-station telecommunication check of control and protection signals
| 17 |  | Converter valve low voltage tests must be completed.
| 18 |  | Air humidity and temperature in valve hall are within expected limits.
| 19 |  | All Normal Power Direction Monopole Low Power Tests as in Annex-C-1 to 10 are successful
| 20 |  | All Reverse Power Direction Monopole Low Power Tests as in Annex-C-11 to 13 are successful
| 21 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (300 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 22 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 23 |  | Return | Ground |  | Ground Return Mode
| 24 |  | Udc Mode | Reduced |  | ±462kV
| 25 |  | Telecom Mode | Operational
| 26 |  | Master Station | Matiari
| 27 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 28 |  |  | B | Standby
| 29 |  | Pole Control Protection (PCP) | A | ACTIVE
| 30 |  |  | B | Standby
| 31 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 32 |  | Station Control Mode | Joint | ACTIVE | Matiari & Lahore will operate jointly.
| 33 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 34 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
DC Filter Switching | 35 | Matiari | Make Sure that Voltages are set in reduced Voltage mode
| 36 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 37 | Matiari & Lahore | Start the Pole, | Power | 200 MW
| 38 |  |  | Ramp Rate: | 50 MW/Min
| 39 |  | Wait to achieve Target Value | Max Time | 5 min
| 40 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 41 |  |  | DC Voltages | 462 kV
| 42 |  |  | RPC Operation | BP-11/13 , HP24/36
| 43 | Lahore |  | Extinction Angle (g) | 17°
| 44 |  |  | DC Voltages | Range to be mentioned
| 45 |  |  | RPC Operation | 1xHP12/24
| 46 | Matiari/Lahore | Verify stable operation & Normal start at reduced voltage with minimum power
| 47 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 48 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 49 | Lahore |  | 1xHP12/24
| 50 | Matiari | Verify | Verify the switches of DC filter are closed.
| 51 |  |  | Initiate the sequence of DC Filter Isolation;
| 52 |  | Verify | Successful isolation of DC filter
| 53 |  |  | No disturbances to the power transmission.
| 54 |  |  | Initiate the sequence of DC Filter Connection
| 55 |  | Verify | Successful connection of DC filter
| 56 |  |  | No disturbances to the power transmission.
| 57 | Lahore | Verify | Verify the switches of DC filter are closed.
| 58 |  |  | Initiate the sequence of DC Filter Isolation;
| 59 |  | Verify | Successful isolation of DC filter
| 60 |  |  | No disturbances to the power transmission.
| 61 |  |  | Initiate the sequence of DC Filter Connection
| 62 |  | Verify | Successful connection of DC filter
| 63 |  |  | No disturbances to the power transmission.
| 64 | Matiari/Lahore | Order Normal Voltages (660kV)
| 65 |  | Verify DC Voltages is ramping up to Normal Voltages without change in power and reach the specified volatges smoothly and without any interruption.
| 66 | Matiari/Lahore | Stop the Pole
| 67 |  | Verify Performance parameters | Retard, Reduced Current
| 68 | Lahore |  | Firing angle (α) | 90°
Loss of 125V DC System C of Pole | 69 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 70 | Matiari & Lahore | Start the Pole, | Power | 200 MW
| 71 |  |  | Ramp Rate: | 50 MW/Min
| 72 |  | Wait to achieve Target Value | Max Time | 5 min
| 73 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 74 |  |  | DC Voltages | 660kV
| 75 |  |  | RPC Operation | BP-11/13 , HP24/36
| 76 | Lahore |  | Extinction Angle (g) | 17°
| 77 |  |  | DC Voltages | Range to be mentioned
| 78 |  |  | RPC Operation | 1xHP12/24
| 79 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 80 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 81 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 82 | Lahore |  | 1xHP12/24
| 83 | Matiari | Switch the incoming to 125 V DC distribution board C (EC1), from system A (U1) to system B (U2), alternative from system B to system A depending on present pre-conditions.
| 84 |  | Verify Continuing Normal operation of power transmission.
| 85 |  | Switch the incoming to 125 V DC distribution board C (EC1), from system B (U2) to system A (U1), alternative from system A to system B depending on present pre-conditions.
| 86 |  | Verify Continuing Normal operation of power transmission.
| 87 | Lahore | Switch the incoming to 125 V DC distribution board C (EC1), from system A (U1) to system B (U2), alternative from system B to system A depending on present pre-conditions.
| 88 |  | Verify Continuing Normal operation of power transmission.
| 89 |  | Switch the incoming to 125 V DC distribution board C (EC1), from system B (U2) to system A (U1), alternative from system A to system B depending on present pre-conditions.
| 90 |  | Verify Continuing Normal operation of power transmission.
Loss of 125V DC System A of Pole | 91 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions. |  |  | If pole is already been operated at 200 MW ignore this step
| 92 | Matiari & Lahore | Start the Pole, | Power | 200 MW
| 93 |  |  | Ramp Rate: | 50 MW/Min
| 94 |  | Wait to achieve Target Value | Max Time | 5 min
| 95 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 96 |  |  | DC Voltages | 660kV
| 97 |  |  | RPC Operation | BP-11/13 , HP24/36
| 98 | Lahore |  | Extinction Angle (g) | 17°
| 99 |  |  | DC Voltages | Range to be mentioned
| 100 |  |  | RPC Operation | 1xHP12/24
| 101 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 102 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 103 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 104 | Lahore |  | 1xHP12/24
| 105 | Matiari | Ramp Up | 200 MW | 300 MW | 50 MW/Min
| 106 | Matiari | Open the 125 V DC system A main switch.
| 107 |  | Verify Continuing Normal operation of power transmission.
| 108 |  | Re-close the 125 V DC system A main switch.
| 109 |  | Verify Continuing Normal operation of power transmission.
| 110 | Lahore | Open the 125 V DC system A main switch.
| 111 |  | Verify Continuing Normal operation of power transmission.
| 112 |  | Re-close the 125 V DC system A main switch.
| 113 |  | Verify Continuing Normal operation of power transmission.
Loss of 125V DC System B of Pole | 114 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions. |  |  | If pole is already been operated at 200 MW ignore this step
| 115 | Matiari & Lahore | Start the Pole | Power | 200 MW
| 116 |  |  | Ramp Rate: | 50 MW/Min
| 117 |  | Wait to achieve Target Value | Max Time | 5 min
| 118 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 119 |  |  | DC Voltages | 660kV
| 120 |  |  | RPC Operation | BP-11/13 , HP24/36
| 121 | Lahore |  | Extinction Angle (g) | 17°
| 122 |  |  | DC Voltages | Range to be mentioned
| 123 |  |  | RPC Operation | 1xHP12/24
| 124 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 125 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 126 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 127 | Lahore |  | 1xHP12/24
| 128 | Matiari | Ramp Up | 200 MW | 300 MW | 50 MW/Min
| 129 | Matiari/Lahore | Open the 125 V DC system B main switch.
| 130 |  | Verify Continuing Normal operation of power transmission.
| 131 |  | Re-close the 125 V DC system B main switch.
| 132 |  | Verify Continuing Normal operation of power transmission.
| 133 | Lahore | Open the 125 V DC system B main switch.
| 134 |  | Verify Continuing Normal operation of power transmission.
| 135 |  | Re-close the 125 V DC system B main switch.
| 136 |  | Verify Continuing Normal operation of power transmission.
Simulated DC Line Fault o nly Matiari | 137 | Matiari/Lahore C/S DC side | Select Joint Current Control, Verify Ready for Operation Conditions.
| 138 | Matiari & Lahore | Start the Pole, | Current | 303 Amps
| 139 |  |  | Ramp Rate: | 100 A/Min
| 140 |  | Wait to achieve Target Value | Max Time | 5 min
| 141 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 142 |  |  | DC Voltages | 660kV
| 143 |  |  | RPC Operation | BP-11/13 , HP24/36
| 144 | Lahore |  | Extinction Angle (g) | 17°
| 145 |  |  | DC Voltages | Range to be mentioned
| 146 |  |  | RPC Operation | 1xHP12/24
| 147 | Matiari/Lahore | Verify stable operation & Normal start at reduced with minimum power
| 148 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 149 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 150 | Lahore |  | 1xHP12/24
| 151 | Matiari | Instruct Test inspector to Simulate a DC Line Fault by activating the DC line protection in PCPA in Matiari.
| 152 | Matiari | Verify | Verify the firing angle has been retarded in Matiari station.
| 153 | Matiari/Lahore |  | Verify that the system quickly recovers within the expected time delays.
| 154 |  | Change all the modified settings back to original value.
| 155 |  | Stop the Pole
| 156 |  | Verify Performance parameters | Retard, Reduced Current
| 157 |  |  | Firing angle (α) | 90°
Simulate Fault of Converter Transformer PT Breaking at Matiari station | 158 | Matiari | Verify pole is in Power Control Mode respectively.
| 159 | Matiari/Lahore | Start the Pole, | Power | 200 MW
| 160 |  |  | Ramp Rate: | 50 MW/Min
| 161 |  | Wait to achieve Target Value | Max Time | 5 min
| 162 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 163 |  |  | DC Voltages | 660kV
| 164 |  |  | RPC Operation | BP-11/13 , HP24/36
| 165 | Lahore |  | Extinction Angle (g) | 17°
| 166 |  |  | DC Voltages | Range to be mentioned
| 167 |  |  | RPC Operation | 1xHP12/24
| 168 | Matiari | Switchover active system to check PCPA and PCPB are healthy.
| 169 |  | Verify PCP-A of system is active in pole.
| 170 |  | Instruct test commander to Simulate Fault of Converter Transformer PT Breaking in active system at Matiari station by pulling out the cable which connected the secondary circuit of converter phase A PT and CTPA.
| 171 |  | Verify | Low AC Voltage Detected
| 172 |  |  | Pole System Switchover by Low AC Voltage On
| 173 |  | Restore the cable, and then verify the PCPA would automatically restore to standby status and PCPB is the active system.
| 174 |  | Instruct test commander to Simulate Fault of Converter Transformer PT Breaking in active system at Matiari station by pulling out the cable which connected the secondary circuit of converter phase A PT and CTPB.
| 175 |  | Verify | Low AC Voltage Detected
| 176 |  |  | Pole System Switchover by Low AC Voltage On
| 177 |  | Restore the cable, and then verify the PCPB would automatically restore to standby status and PCPA is the active system.
| 178 | Matiari | Stop the Pole
| 179 |  | Verify Performance parameters | Retard, Reduced Current
| 180 | Lahore |  | Firing angle (α) | 90°
Simulate Fault of Converter Transformer PT Breaking at Lahore station | 181 | Matiari | Verify pole is in Power Control Mode respectively.
| 182 | Matiari/Lahore | Start the Pole | Power | 200 MW
| 183 |  |  | Ramp Rate: | 50 MW/Min
| 184 |  | Wait to achieve Target Value | Max Time | 5 min
| 185 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 186 |  |  | DC Voltages | 660kV
| 187 |  |  | RPC Operation | BP-11/13 , HP24/36
| 188 | Lahore |  | Extinction Angle (g) | 17°
| 189 |  |  | DC Voltages | Range to be mentioned
| 190 |  |  | RPC Operation | 1xHP12/24
| 191 | Lahore | Switchover active system to check PCPA and PCPB are healthy.
| 192 |  | Verify PCP-A of system is active in pole.
| 193 |  | Instruct test commander to Simulate Fault of Converter Transformer PT Breaking in active system at Matiari station by pulling out the cable which connected the secondary circuit of converter phase A PT and CTPA
| 194 |  | Verify | Low AC Voltage Detected
| 195 |  |  | Pole System Switchover by Low AC Voltage On
| 196 |  | Restore the cable, and then verify the PCPA would automatically restore to standby status and PCPB is the active system.
| 197 |  | Instruct test commander to Simulate Fault of Converter Transformer PT Breaking in active system at Matiari station by pulling out the cable which connected the secondary circuit of converter phase A PT and CTPB.
| 198 |  | Verify | Low AC Voltage Detected
| 199 |  |  | Pole System Switchover by Low AC Voltage On
| 200 |  | Restore the cable, and then verify the PCPB would automatically restore to standby status and PCPA is the active system.
| 201 | Matiari | Stop the Pole
| 202 |  | Verify Performance parameters | Retard, Reduced Current
| 203 | Lahore |  | Firing angle (α) | 90°
Simulate Fault of DC Line PT Breaking at Matiari station | 204 | Matiari | Verify pole is in Power Control Mode respectively.
| 205 | Matiari/Lahore | Start the Pole | Current | 200 MW
| 206 |  |  | Ramp Rate: | 50 MW/Min
| 207 |  | Wait to achieve Target Value | Max Time | 5 min
| 208 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 209 |  |  | DC Voltages | 660kV
| 210 |  |  | RPC Operation | BP-11/13 , HP24/36
| 211 | Lahore |  | Extinction Angle (g) | 17°
| 212 |  |  | DC Voltages | Range to be mentioned
| 213 |  |  | RPC Operation | 1xHP12/24
| 214 | Matiari | Switchover active system to check PCPA and PCPB are healthy.
| 215 |  | Verify PCP-A of system is active in pole.
| 216 |  | Instruct test commander to Simulate Fault of DC Line PT Breaking in active system at Matiari station by pulling out the signal which connected the secondary circuit of DC line PT and PCPA.
| 217 |  | Verify | Pole DC Line Voltage Measurement Value Error
| 218 |  |  | Pole Active System Switchover.
| 219 |  | Restore the cable, and then verify the PCPA would automatically restore to standby status and PCPB is the active system.
| 220 |  | Instruct test commander to Simulate Fault of DC Line PT Breaking in active system at Matiari station by pulling out the signal which connected the secondary circuit of DC line PT and PCPB.
| 221 |  | Verify | Pole DC Line Voltage Measurement Value Error
| 222 |  |  | Pole Active System Switchover.
| 223 |  | Restore the cable, and then verify the PCPB would automatically restore to standby status and PCPA is the active system.
| 224 | Matiari | Stop the Pole
| 225 |  | Verify Performance parameters | Retard, Reduced Current
| 226 | Lahore |  | Firing angle (α) | 90°
Simulate Fault of DC Line PT Breaking at Lahore station | 227 | Lahore | Verify pole is in Power Control Mode respectively.
| 228 | Matiari/Lahore | Start the Pole | Current | 200 MW
| 229 |  |  | Ramp Rate: | 50 MW/Min
| 230 |  | Wait to achieve Target Value | Max Time | 5 min
| 231 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 232 |  |  | DC Voltages | 660kV
| 233 |  |  | RPC Operation | BP-11/13 , HP24/36
| 234 | Lahore |  | Extinction Angle (g) | 17°
| 235 |  |  | DC Voltages | Range to be mentioned
| 236 |  |  | RPC Operation | 1xHP12/24
| 237 | Lahore | Switchover active system to check PCPA and PCPB are healthy.
| 238 |  | Verify PCP-A of system is active in pole.
| 239 |  | Instruct test commander to Simulate Fault of DC Line PT Breaking in active system at Matiari station by pulling out the signal which connected the secondary circuit of DC line PT and PCPA
| 240 |  | Verify | Pole DC Line Voltage Measurement Value Error
| 241 |  |  | Pole Active System Switchover.
| 242 |  | Restore the cable, and then verify the PCPA would automatically restore to standby status and PCPB is the active system.
| 243 |  | Instruct test commander to Simulate Fault of DC Line PT Breaking in active system at Matiari station by pulling out the signal which connected the secondary circuit of DC line PT and PCPB.
| 244 |  | Verify | Pole DC Line Voltage Measurement Value Error
| 245 |  |  | Pole Active System Switchover.
| 246 |  | Restore the cable, and then verify the PCPB would automatically restore to standby status and PCPA is the active system.
| 247 | Matiari | Stop the Pole
| 248 |  | Verify Performance parameters | Retard, Reduced Current
| 249 | Lahore |  | Firing angle (α) | 90°
Simulate NO ACTIVE signal loss of pole control changeover devi ce | 250 | Lahore | Verify pole is in Power Control Mode respectively.
| 251 | Matiari/Lahore | Start the Pole-2 | Current | 200 MW
| 252 |  |  | Ramp Rate: | 50 MW/Min
| 253 |  | Wait to achieve Target Value | Max Time | 5 min
| 254 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 255 |  |  | DC Voltages | 660kV
| 256 |  |  | RPC Operation | BP-11/13 , HP24/36
| 257 | Lahore |  | Extinction Angle (g) | 17°
| 258 |  |  | DC Voltages | Range to be mentioned
| 259 |  |  | RPC Operation | 1xHP12/24
| 260 | Matiari | Switchover active system to check PCPA and PCPB are healthy.
| 261 |  | Verify PCP-A of system is active in pole.
| 262 |  | Instruct test commander to Simulate NO ACTIVE signal loss of pole control changeover device at Matiari station by pulling out the signal which send the NO ACTIVE signal cable.
| 263 |  | Verify | Pole keep stable operation.
| 264 |  | Restore the cable, and then verify the PCPA would automatically restore to standby status and PCPB is the active system.
| 265 | Lahore | Switchover active system to check PCPA and PCPB are healthy.
| 266 |  | Verify PCP-A of system is active in pole.
| 267 |  | Instruct test commander to Simulate NO ACTIVE signal loss of pole control changeover device at Lahore station by pulling out the signal which send the NO ACTIVE signal cable.
| 268 |  | Verify | Pole 2 keep stable operation.
| 269 |  | Restore the cable, and then verify the PCPB would automatically restore to standby status and PCPA is the active system.
| 270 | Matiari | Stop the Pole
| 271 |  | Verify Performance parameters | Retard, Reduced Current
| 272 | Lahore |  | Firing angle (α) | 90°
Test Acceptance Criteria | 273 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 274 |  | All Operations executed successfully
| 275 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 276 |  | All thyristor check-back signals are available.
| 277 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 278 |  | Measuring quantities are available and the values are within the specified range and phase.
| 279 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 280 |  | No Stuck Condition
| 281 |  | No False Tripping by DC Protection System
| 282 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 283 |  | No Tripping in AC side of converter Station
kkkk

## Control Pulse
Monopole Low Power Tests
15-Control Pulse Loss Failure, Normal Power Direction, Joint Power Control
Test Objective | The test objective is to check the DC system operation and system switchover during control pulse loss failure.
Condition | Sr. No. | Station | Action | Equipment/Configuration | State of Equipment/configuration | Description
Pre-Test Conditions & Configurations (AC/DC) | 1 | AC side at Matiari & Lahore C/S | Voltage Limits | Utmost efforts will be made to maintain the voltages within ±5% range. However, reactive compensation devices installed at both converter stations can be used, if needed, to control the voltages keeping in view the then prevailing system conditions.
| 2 |  | AC Yard of Lahore & Matiari Converter Station is in normal Position |  | CLOSED State | All bays including Filter Banks are complete and energized with no component in maintenance state.
| 3 | DC Side switchyard status | During Pole-I testing
| 4 |  | See Status Table "P1-GR" |  |  | Ground Return Mode
| 5 |  | See Status Table "Mat-P2-ISOLAT" for Matiari and "Lah-P2-ISOLAT" for Lahore. |  |  | Isolation Mode
| 6 |  | During Pole-II testing
| 7 |  | See Status Table "Mat-P1-ISOLAT" for Matiari and "Lah-P1-ISOLAT" for Lahore. |  |  | Isolation Mode
| 8 |  | See Status Table "P2-GR" |  |  | Ground Return Mode
| 9 | General Preconditions | Converter transformer protection and the charging protection of corresponding converter AC bus breaker are put into operation.
| 10 |  | Visual inspections of AC switchyard, AC filter yard, DC yard and DC valve hall prior first energization or switching.
| 11 |  | All electrical connections are available.
| 12 |  | Correct grounding of all equipment is available.
| 13 |  | Thyristor valve cooling in operation for 24 hours, no water leakage observed.
| 14 |  | Thyristor valves and valve hall is cleaned.
| 15 |  | Verify Sequence of Events Recorder (SER) and make sure that no relevant alarms are present, and all systems are operational.
Inter-station telecommunication check of control and protection signals
| 17 |  | Converter valve low voltage tests must be completed.
| 18 |  | Air humidity and temperature in valve hall are within expected limits.
| 19 |  | All Normal Power Direction Monopole Low Power Tests as in Annex-C-1 to 10 are successful
| 20 |  | All Reverse Power Direction Monopole Low Power Tests as in Annex-C-11 to 14 are successful
| 21 |  | Both sides AC system of Matiari & Lahore C/S are capable to supply and accept the power (200 MW) for the test. Availability of N-1 contingency on parallel AC corridor. AC system short circuit level has been measured at both Matiari and Lahore converter stations and it is confirmed to be suitable for the tested power.
| 22 | DC Configuration Selection (Automatically apply to both Lahore and Matiari) | Direction | Normal |  | Matiari to Lahore
| 23 |  | Return | Ground |  | Ground Return Mode
| 24 |  | Udc Mode | Normal |  | ±660kV
| 25 |  | Telecom Mode | Operational
| 26 |  | Master Station | Matiari
| 27 | Configuration Setting at Lahore & Matiari C/S DC side | Station Control (SC) | A | ACTIVE | Can be changed to B during test
| 28 |  |  | B | Standby
| 29 |  | Pole Control Protection (PCP) | A | ACTIVE
| 30 |  |  | B | Standby
| 31 |  | Transmission Control Mode | Power | ACTIVE | HVDC will operate in power control mode.
| 32 |  | Station Control Mode | Joint | ACTIVE | Matiari & Lahore will operate jointly.
| 33 |  | Reactive Power Control Mode | Automatic | ACTIVE | Automatically Switch in/out the AC Filters/Reactors
| 34 |  | Reactive Power Control Variable | Q-Control | ACTIVE | Reactive Power exchange between AC Yard of Converter Station and NTDC system will be automatically controlled.
Testing Start Up Sequence
Multiple (>5) Pulses Loss Fault at Inverter in Ground Return | 35 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 36 | Matiari & Lahore | Start the Pole, | Power | 200 MW
| 37 |  |  | Ramp Rate: | 50 MW/Min
| 38 |  | Wait to achieve Target Value | Max Time | 5 min
| 39 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 40 |  |  | DC Voltages | 660kV
| 41 |  |  | RPC Operation | BP-11/13 , HP24/36
| 42 | Lahore |  | Extinction Angle (g) | 17°
| 43 |  |  | DC Voltages | Range to be mentioned
| 44 |  |  | RPC Operation | 1xHP12/24
| 45 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 46 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 47 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 48 | Lahore |  | 1xHP12/24
| 49 | Lahore | Instruct Test Commander to Simulate more than five consecutive firing pulses loss in LAHORE by pulling out a CP signal optical fiber from PCP A system to VBE A system. PCP B system is out of service.
| 50 | Lahore | Verify | Advancing of Gamma
| 51 |  |  | Switch to the standby pole control system
| 52 |  |  | Y-block of the converter
| 53 |  |  | Trip of the AC circuit breaker(s) feeding the converter transformer.
| 54 |  |  | Pole isolation.
| 55 |  |  | Trip of the AC Filters breakers by RPC.
| 56 |  |  | Start breaker failure protection.
| 57 |  |  | Set lockout relay for the tripped AC circuit breaker(s).
| 58 | Matiari |  | Lock the DC-line protection. (?)
| 59 |  |  | Y-block of the converter.
| 60 |  |  | Trip of the AC Filters breakers by RPC.
| 61 |  |  | Set lockout relay for the tripped AC circuit breaker(s).
Multiple (>5) Pulses Loss Fault at Rectifier in Ground Return | 62 |  | Initiate the sequence for transfer from Metallic to Ground Return.
| 63 | Matiari/Lahore C/S DC side | Verify Ready for Operation Conditions.
| 64 | Matiari & Lahore | Start the Pole | Power | 200 MW
| 65 |  |  | Ramp Rate: | 50 MW/Min
| 66 |  | Wait to achieve Target Value | Max Time | 5 min
| 67 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 68 |  |  | DC Voltages | 660kV
| 69 |  |  | RPC Operation | BP-11/13 , HP24/36
| 70 | Lahore |  | Extinction Angle (g) | 17°
| 71 |  |  | DC Voltages | Range to be mentioned
| 72 |  |  | RPC Operation | 1xHP12/24
| 73 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 74 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 75 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 76 | Lahore |  | 1xHP12/24
| 77 | Matiari | Instruct Test Commander to Simulate more than five consecutive firing pulses loss in Matiari by pulling out a CP signal optical fiber from PCP B system to VBE B system. PCP A system is out of service.
| 78 | Matiari | Verify | Switch to the standby pole control system
| 79 |  |  | Y-block of the converter
| 80 |  |  | Trip of the AC circuit breaker(s) feeding the converter transformer.
| 81 |  |  | Pole isolation.
| 82 |  |  | Trip of the AC Filters breakers by RPC.
| 83 |  |  | Start breaker failure protection.
| 84 |  |  | Set lockout relay for the tripped AC circuit breaker(s).
| 85 | Lahore |  | Normal Y-stop sequence.
| 86 |  |  | Trip of the AC Filters breakers by RPC.
Multiple (>5) Pulses Loss Fault at Inverter in Metallic Return | 87 | Matiari/Lahore | Initiate the sequence for transfer from Ground to Metallic Return.
| 88 |  | Verify Ready for Operation Conditions.
| 89 | Matiari/Lahore | Start the Pole-1, | Power | 200 MW
| 90 |  |  | Ramp Rate: | 50 MW/Min
| 91 |  | Wait to achieve Target Value | Max Time | 5 min
| 92 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 93 |  |  | DC Voltages | 660kV
| 94 |  |  | RPC Operation | BP-11/13 , HP24/36
| 95 | Lahore |  | Extinction Angle (g) | 17°
| 96 |  |  | DC Voltages | Range to be mentioned
| 97 |  |  | RPC Operation | 1xHP12/24
| 98 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 99 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 100 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 101 | Lahore |  | 1xHP12/24
| 102 | Lahore | Instruct Test Commander to Simulate more than five consecutive firing pulses loss in LAHORE by pulling out a CP signal optical fiber from PCP A system to VBE A system. PCP B system is out of service.
| 103 | Lahore | Verify | Advancing of Gamma
| 104 |  |  | Switch to the standby pole control system
| 105 |  |  | Y-block of the converter
| 106 |  |  | Trip of the AC circuit breaker(s) feeding the converter transformer.
| 107 |  |  | Pole isolation.
| 108 |  |  | Trip of the AC Filters breakers by RPC.
| 109 |  |  | Start breaker failure protection.
| 110 |  |  | Set lockout relay for the tripped AC circuit breaker(s).
| 111 | Matiari |  | Lock the DC-line protection. (?)
| 112 |  |  | Y-block of the converter.
| 113 |  |  | Trip of the AC Filters breakers by RPC.
| 114 |  |  | Set lockout relay for the tripped AC circuit breaker(s).
Multiple (>5) Pulses Loss Fault at Rectifier in Metallic Return | 115 | Matiari/Lahore | Verify Ready for Operation Conditions.
| 116 | Matiari/Lahore | Start the Pole, | Power | 200 MW
| 117 |  |  | Ramp Rate: | 50 MW/Min
| 118 |  | Wait to achieve Target Value | Max Time | 5 min
| 119 | Matiari | Verify Performance indicators | Firing angle (α) | 15°±2.5°
| 120 |  |  | DC Voltages | 660kV
| 121 |  |  | RPC Operation | BP-11/13 , HP24/36
| 122 | Lahore |  | Extinction Angle (g) | 17°
| 123 |  |  | DC Voltages | Range to be mentioned
| 124 |  |  | RPC Operation | 1xHP12/24
| 125 | Matiari/Lahore | Verify stable operation & Normal start at minimum power
| 126 |  | Perform normal inspections (visual and acoustical) while pole is deblocked.
| 127 | Matiari | Verify RPC action | BP-11/13, HP-24/36
| 128 | Lahore |  | 1xHP12/24
| 129 | Lahore | Instruct Test Commander to Simulate more than five consecutive firing pulses loss in LAHORE by pulling out a CP signal optical fiber from PCP A system to VBE A system. PCP B system is out of service.
| 130 | Lahore | Verify | Advancing of Gamma
| 131 |  |  | Switch to the standby pole control system
| 132 |  |  | Y-block of the converter
| 133 |  |  | Trip of the AC circuit breaker(s) feeding the converter transformer.
| 134 |  |  | Pole isolation.
| 135 |  |  | Trip of the AC Filters breakers.
| 136 |  |  | Start breaker failure protection.
| 137 |  |  | Set lockout relay for the tripped AC circuit breaker(s).
| 138 | Matiari |  | Lock the DC-line protection. (?)
| 139 |  |  | Y-block of the converter.
| 140 |  |  | Trip of the AC Filters breakers.
| 141 |  |  | Set lockout relay for the tripped AC circuit breaker(s).
Test Acceptance Criteria | 142 | Matiari/Lahore C/S | The voltage of the AC system should be within the specified limits (450-550kV)
| 143 |  | All Operations executed successfully
| 144 |  | The synchronizing voltage and the phasing of the firing control signals are correct.
| 145 |  | All thyristor check-back signals are available.
| 146 |  | Measuring system and controls remain operational. No transients on switchover of PCP or SC systems.
| 147 |  | Measuring quantities are available and the values are within the specified range and phase.
| 148 |  | No abnormal corona discharges and no operation of surge arresters shall occur at energized equipment.
| 149 |  | No Stuck Condition
| 150 |  | No False Tripping by DC Protection System
| 151 |  | All the sequence as recorded in OWS should be documented, All the Charts related to pole power,current, voltages, firing angles and extinction angles, tap positions. Should be recorded and documented. TFR data in Comtrade format to be captured and recorded.
| 152 |  | No Tripping in AC side of converter Station
kkkk